## Summary
Villa Somalia Hybrid Power Plant - SCADA I/O List (Annex A)
Ref. BFE/PR/26/01-SC-001 Rev 0 - Issued for approval
Generated from the SCADA tag database that drives the HMI screens. Modbus addresses are placeholders until vendor register maps are received.
Area | Analogue in | Digital in | Setpoints (AO) | Commands (DO) | Total
11kV GIS Combiner Panel | 118 | 167 | 0 | 24 | 309
Transformers | 18 | 31 | 0 | 0 | 49
Remote RMUs (President / P.M.) | 8 | 40 | 0 | 4 | 52
LV Distribution Boards | 73 | 76 | 0 | 6 | 155
Diesel Generators | 44 | 44 | 2 | 12 | 102
PV Plant / Inverters | 195 | 38 | 8 | 10 | 251
Weather Station | 9 | 2 | 0 | 0 | 11
Battery Energy Storage | 92 | 37 | 4 | 5 | 138
Fire Detection & Suppression | 2 | 35 | 0 | 2 | 39
UPS & Auxiliary Power | 3 | 12 | 0 | 0 | 15
Communications & Cybersecurity | 1 | 19 | 0 | 0 | 20
Power Plant Controller | 13 | 2 | 6 | 2 | 23
Total | 576 | 503 | 20 | 65 | 1164
Alarm priority: 1 critical (trips, fire, loss of supply) - 2 high - 3 medium - 4 low.
Tag format: AREA.EQUIPMENT.SIGNAL

## I-O List
Tag | Area | Equipment | Signal | Type | Description | Unit | Range | Source device | Protocol | Address / LN | Alarm | Priority | LoLo | Lo | Hi | HiHi
GIS.AH1.CB_CLOSED | 11kV GIS Combiner Panel | AH1 | CB_CLOSED | DI | QF11 VCB closed |  |  | RLY-AH1 | IEC 61850 MMS | GISAH1CTRL/XCBR1.Pos.stVal
GIS.AH1.CB_OPEN | 11kV GIS Combiner Panel | AH1 | CB_OPEN | DI | QF11 VCB open |  |  | RLY-AH1 | IEC 61850 MMS | GISAH1CTRL/XCBR1.Pos.stVal
GIS.AH1.CB_TRIPPED | 11kV GIS Combiner Panel | AH1 | CB_TRIPPED | DI | QF11 VCB tripped (protection) |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.CB_SPRING | 11kV GIS Combiner Panel | AH1 | CB_SPRING | DI | QF11 VCB spring charged |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 0 | 3
GIS.AH1.TCS_FAIL | 11kV GIS Combiner Panel | AH1 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH1.LR_REMOTE | 11kV GIS Combiner Panel | AH1 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 0 | 4
GIS.AH1.CMD_OPEN | 11kV GIS Combiner Panel | AH1 | CMD_OPEN | DO | QF11 VCB open command |  |  | RLY-AH1 | IEC 61850 MMS | GISAH1CTRL/XCBR1.Pos.Oper
GIS.AH1.CMD_CLOSE | 11kV GIS Combiner Panel | AH1 | CMD_CLOSE | DO | QF11 VCB close command |  |  | RLY-AH1 | IEC 61850 MMS | GISAH1CTRL/XCBR1.Pos.Oper
GIS.AH1.DS_CLOSED | 11kV GIS Combiner Panel | AH1 | DS_CLOSED | DI | QL11 3-position switch - closed (line) |  |  | RLY-AH1 | IEC 61850 MMS | GISAH1CTRL/XSWI1.Pos.stVal
GIS.AH1.ES_EARTHED | 11kV GIS Combiner Panel | AH1 | ES_EARTHED | DI | QL11 3-position switch - earthed |  |  | RLY-AH1 | IEC 61850 MMS | GISAH1CTRL/XSWI2.Pos.stVal
GIS.AH1.VPIS | 11kV GIS Combiner Panel | AH1 | VPIS | DI | Voltage presence indicator (DXN-12Q) |  |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.SF6_LOW | 11kV GIS Combiner Panel | AH1 | SF6_LOW | DI | SF6 gas pressure low (alarm) |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH1.SF6_LOLO | 11kV GIS Combiner Panel | AH1 | SF6_LOLO | DI | SF6 gas pressure low-low (block) |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.RLY_HEALTHY | 11kV GIS Combiner Panel | AH1 | RLY_HEALTHY | DI | Protection relay healthy (watchdog) |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 0 | 1
GIS.AH1.MCB_TRIP | 11kV GIS Combiner Panel | AH1 | MCB_TRIP | DI | Aux supply MCB tripped |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH1.SPD_OPER | 11kV GIS Combiner Panel | AH1 | SPD_OPER | DI | Surge arrester (HY5WS-17/50) operated |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 3
GIS.AH1.PROT_50 | 11kV GIS Combiner Panel | AH1 | PROT_50 | DI | Trip 50/51 phase overcurrent |  |  | RLY-AH1 | IEC 61850 MMS | GISAH1PROT/PTOC1.Op | On state = 1 | 1
GIS.AH1.PROT_50N | 11kV GIS Combiner Panel | AH1 | PROT_50N | DI | Trip 50N/51N earth fault |  |  | RLY-AH1 | IEC 61850 MMS | GISAH1PROT/PTOC2.Op | On state = 1 | 1
GIS.AH1.PROT_50G | 11kV GIS Combiner Panel | AH1 | PROT_50G | DI | Trip 51G sensitive earth fault (ZSCT) |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.PROT_46 | 11kV GIS Combiner Panel | AH1 | PROT_46 | DI | Trip 46 negative sequence / broken conductor |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.PROT_27 | 11kV GIS Combiner Panel | AH1 | PROT_27 | DI | Trip 27 undervoltage |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.PROT_59 | 11kV GIS Combiner Panel | AH1 | PROT_59 | DI | Trip 59 overvoltage |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.PROT_81 | 11kV GIS Combiner Panel | AH1 | PROT_81 | DI | Trip 81 O/U frequency |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.PROT_32 | 11kV GIS Combiner Panel | AH1 | PROT_32 | DI | Trip 32 reverse power |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.LOCKOUT_86 | 11kV GIS Combiner Panel | AH1 | LOCKOUT_86 | DI | Lockout relay 86 operated |  |  | RLY-AH1 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH1.CMD_RESET | 11kV GIS Combiner Panel | AH1 | CMD_RESET | DO | Protection / lockout reset |  |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.I_L1 | 11kV GIS Combiner Panel | AH1 | I_L1 | AI | Current L1 | A |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.I_L2 | 11kV GIS Combiner Panel | AH1 | I_L2 | AI | Current L2 | A |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.I_L3 | 11kV GIS Combiner Panel | AH1 | I_L3 | AI | Current L3 | A |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.I_N | 11kV GIS Combiner Panel | AH1 | I_N | AI | Neutral / residual current | A |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.U_L12 | 11kV GIS Combiner Panel | AH1 | U_L12 | AI | Voltage L12 | kV |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.U_L23 | 11kV GIS Combiner Panel | AH1 | U_L23 | AI | Voltage L23 | kV |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.U_L31 | 11kV GIS Combiner Panel | AH1 | U_L31 | AI | Voltage L31 | kV |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.P | 11kV GIS Combiner Panel | AH1 | P | AI | Active power | kW |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.Q | 11kV GIS Combiner Panel | AH1 | Q | AI | Reactive power | kvar |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.S | 11kV GIS Combiner Panel | AH1 | S | AI | Apparent power | kVA |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.PF | 11kV GIS Combiner Panel | AH1 | PF | AI | Power factor |  |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.F | 11kV GIS Combiner Panel | AH1 | F | AI | Frequency | Hz |  | RLY-AH1 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.AH1.E_IMP | 11kV GIS Combiner Panel | AH1 | E_IMP | AI | Active energy import | MWh |  | RLY-AH1 | IEC 61850 MMS
GIS.AH1.E_EXP | 11kV GIS Combiner Panel | AH1 | E_EXP | AI | Active energy export | MWh |  | RLY-AH1 | IEC 61850 MMS
GIS.AH2.CB_CLOSED | 11kV GIS Combiner Panel | AH2 | CB_CLOSED | DI | QF12 VCB closed |  |  | RLY-AH2 | IEC 61850 MMS | GISAH2CTRL/XCBR1.Pos.stVal
GIS.AH2.CB_OPEN | 11kV GIS Combiner Panel | AH2 | CB_OPEN | DI | QF12 VCB open |  |  | RLY-AH2 | IEC 61850 MMS | GISAH2CTRL/XCBR1.Pos.stVal
GIS.AH2.CB_TRIPPED | 11kV GIS Combiner Panel | AH2 | CB_TRIPPED | DI | QF12 VCB tripped (protection) |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.CB_SPRING | 11kV GIS Combiner Panel | AH2 | CB_SPRING | DI | QF12 VCB spring charged |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 0 | 3
GIS.AH2.TCS_FAIL | 11kV GIS Combiner Panel | AH2 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH2.LR_REMOTE | 11kV GIS Combiner Panel | AH2 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 0 | 4
GIS.AH2.CMD_OPEN | 11kV GIS Combiner Panel | AH2 | CMD_OPEN | DO | QF12 VCB open command |  |  | RLY-AH2 | IEC 61850 MMS | GISAH2CTRL/XCBR1.Pos.Oper
GIS.AH2.CMD_CLOSE | 11kV GIS Combiner Panel | AH2 | CMD_CLOSE | DO | QF12 VCB close command |  |  | RLY-AH2 | IEC 61850 MMS | GISAH2CTRL/XCBR1.Pos.Oper
GIS.AH2.DS_CLOSED | 11kV GIS Combiner Panel | AH2 | DS_CLOSED | DI | QL12 3-position switch - closed (line) |  |  | RLY-AH2 | IEC 61850 MMS | GISAH2CTRL/XSWI1.Pos.stVal
GIS.AH2.ES_EARTHED | 11kV GIS Combiner Panel | AH2 | ES_EARTHED | DI | QL12 3-position switch - earthed |  |  | RLY-AH2 | IEC 61850 MMS | GISAH2CTRL/XSWI2.Pos.stVal
GIS.AH2.VPIS | 11kV GIS Combiner Panel | AH2 | VPIS | DI | Voltage presence indicator (DXN-12Q) |  |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.SF6_LOW | 11kV GIS Combiner Panel | AH2 | SF6_LOW | DI | SF6 gas pressure low (alarm) |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH2.SF6_LOLO | 11kV GIS Combiner Panel | AH2 | SF6_LOLO | DI | SF6 gas pressure low-low (block) |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.RLY_HEALTHY | 11kV GIS Combiner Panel | AH2 | RLY_HEALTHY | DI | Protection relay healthy (watchdog) |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 0 | 1
GIS.AH2.MCB_TRIP | 11kV GIS Combiner Panel | AH2 | MCB_TRIP | DI | Aux supply MCB tripped |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH2.SPD_OPER | 11kV GIS Combiner Panel | AH2 | SPD_OPER | DI | Surge arrester (HY5WS-17/50) operated |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 3
GIS.AH2.PROT_50 | 11kV GIS Combiner Panel | AH2 | PROT_50 | DI | Trip 50/51 phase overcurrent |  |  | RLY-AH2 | IEC 61850 MMS | GISAH2PROT/PTOC1.Op | On state = 1 | 1
GIS.AH2.PROT_50N | 11kV GIS Combiner Panel | AH2 | PROT_50N | DI | Trip 50N/51N earth fault |  |  | RLY-AH2 | IEC 61850 MMS | GISAH2PROT/PTOC2.Op | On state = 1 | 1
GIS.AH2.PROT_50G | 11kV GIS Combiner Panel | AH2 | PROT_50G | DI | Trip 51G sensitive earth fault (ZSCT) |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.PROT_46 | 11kV GIS Combiner Panel | AH2 | PROT_46 | DI | Trip 46 negative sequence / broken conductor |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.PROT_27 | 11kV GIS Combiner Panel | AH2 | PROT_27 | DI | Trip 27 undervoltage |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.PROT_59 | 11kV GIS Combiner Panel | AH2 | PROT_59 | DI | Trip 59 overvoltage |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.PROT_81 | 11kV GIS Combiner Panel | AH2 | PROT_81 | DI | Trip 81 O/U frequency |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.PROT_32 | 11kV GIS Combiner Panel | AH2 | PROT_32 | DI | Trip 32 reverse power |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.LOCKOUT_86 | 11kV GIS Combiner Panel | AH2 | LOCKOUT_86 | DI | Lockout relay 86 operated |  |  | RLY-AH2 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH2.CMD_RESET | 11kV GIS Combiner Panel | AH2 | CMD_RESET | DO | Protection / lockout reset |  |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.I_L1 | 11kV GIS Combiner Panel | AH2 | I_L1 | AI | Current L1 | A |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.I_L2 | 11kV GIS Combiner Panel | AH2 | I_L2 | AI | Current L2 | A |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.I_L3 | 11kV GIS Combiner Panel | AH2 | I_L3 | AI | Current L3 | A |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.I_N | 11kV GIS Combiner Panel | AH2 | I_N | AI | Neutral / residual current | A |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.U_L12 | 11kV GIS Combiner Panel | AH2 | U_L12 | AI | Voltage L12 | kV |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.U_L23 | 11kV GIS Combiner Panel | AH2 | U_L23 | AI | Voltage L23 | kV |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.U_L31 | 11kV GIS Combiner Panel | AH2 | U_L31 | AI | Voltage L31 | kV |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.P | 11kV GIS Combiner Panel | AH2 | P | AI | Active power | kW |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.Q | 11kV GIS Combiner Panel | AH2 | Q | AI | Reactive power | kvar |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.S | 11kV GIS Combiner Panel | AH2 | S | AI | Apparent power | kVA |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.PF | 11kV GIS Combiner Panel | AH2 | PF | AI | Power factor |  |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.F | 11kV GIS Combiner Panel | AH2 | F | AI | Frequency | Hz |  | RLY-AH2 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.AH2.E_IMP | 11kV GIS Combiner Panel | AH2 | E_IMP | AI | Active energy import | MWh |  | RLY-AH2 | IEC 61850 MMS
GIS.AH2.E_EXP | 11kV GIS Combiner Panel | AH2 | E_EXP | AI | Active energy export | MWh |  | RLY-AH2 | IEC 61850 MMS
GIS.AH3.CB_CLOSED | 11kV GIS Combiner Panel | AH3 | CB_CLOSED | DI | QF13 VCB closed |  |  | RLY-AH3 | IEC 61850 MMS | GISAH3CTRL/XCBR1.Pos.stVal
GIS.AH3.CB_OPEN | 11kV GIS Combiner Panel | AH3 | CB_OPEN | DI | QF13 VCB open |  |  | RLY-AH3 | IEC 61850 MMS | GISAH3CTRL/XCBR1.Pos.stVal
GIS.AH3.CB_TRIPPED | 11kV GIS Combiner Panel | AH3 | CB_TRIPPED | DI | QF13 VCB tripped (protection) |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.CB_SPRING | 11kV GIS Combiner Panel | AH3 | CB_SPRING | DI | QF13 VCB spring charged |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 0 | 3
GIS.AH3.TCS_FAIL | 11kV GIS Combiner Panel | AH3 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH3.LR_REMOTE | 11kV GIS Combiner Panel | AH3 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 0 | 4
GIS.AH3.CMD_OPEN | 11kV GIS Combiner Panel | AH3 | CMD_OPEN | DO | QF13 VCB open command |  |  | RLY-AH3 | IEC 61850 MMS | GISAH3CTRL/XCBR1.Pos.Oper
GIS.AH3.CMD_CLOSE | 11kV GIS Combiner Panel | AH3 | CMD_CLOSE | DO | QF13 VCB close command |  |  | RLY-AH3 | IEC 61850 MMS | GISAH3CTRL/XCBR1.Pos.Oper
GIS.AH3.DS_CLOSED | 11kV GIS Combiner Panel | AH3 | DS_CLOSED | DI | QL13 3-position switch - closed (line) |  |  | RLY-AH3 | IEC 61850 MMS | GISAH3CTRL/XSWI1.Pos.stVal
GIS.AH3.ES_EARTHED | 11kV GIS Combiner Panel | AH3 | ES_EARTHED | DI | QL13 3-position switch - earthed |  |  | RLY-AH3 | IEC 61850 MMS | GISAH3CTRL/XSWI2.Pos.stVal
GIS.AH3.VPIS | 11kV GIS Combiner Panel | AH3 | VPIS | DI | Voltage presence indicator (DXN-12Q) |  |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.SF6_LOW | 11kV GIS Combiner Panel | AH3 | SF6_LOW | DI | SF6 gas pressure low (alarm) |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH3.SF6_LOLO | 11kV GIS Combiner Panel | AH3 | SF6_LOLO | DI | SF6 gas pressure low-low (block) |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.RLY_HEALTHY | 11kV GIS Combiner Panel | AH3 | RLY_HEALTHY | DI | Protection relay healthy (watchdog) |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 0 | 1
GIS.AH3.MCB_TRIP | 11kV GIS Combiner Panel | AH3 | MCB_TRIP | DI | Aux supply MCB tripped |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH3.SPD_OPER | 11kV GIS Combiner Panel | AH3 | SPD_OPER | DI | Surge arrester (HY5WS-17/50) operated |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 3
GIS.AH3.PROT_50 | 11kV GIS Combiner Panel | AH3 | PROT_50 | DI | Trip 50/51 phase overcurrent |  |  | RLY-AH3 | IEC 61850 MMS | GISAH3PROT/PTOC1.Op | On state = 1 | 1
GIS.AH3.PROT_50N | 11kV GIS Combiner Panel | AH3 | PROT_50N | DI | Trip 50N/51N earth fault |  |  | RLY-AH3 | IEC 61850 MMS | GISAH3PROT/PTOC2.Op | On state = 1 | 1
GIS.AH3.PROT_50G | 11kV GIS Combiner Panel | AH3 | PROT_50G | DI | Trip 51G sensitive earth fault (ZSCT) |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.PROT_46 | 11kV GIS Combiner Panel | AH3 | PROT_46 | DI | Trip 46 negative sequence / broken conductor |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.PROT_27 | 11kV GIS Combiner Panel | AH3 | PROT_27 | DI | Trip 27 undervoltage |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.PROT_59 | 11kV GIS Combiner Panel | AH3 | PROT_59 | DI | Trip 59 overvoltage |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.PROT_81 | 11kV GIS Combiner Panel | AH3 | PROT_81 | DI | Trip 81 O/U frequency |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.PROT_32 | 11kV GIS Combiner Panel | AH3 | PROT_32 | DI | Trip 32 reverse power |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.LOCKOUT_86 | 11kV GIS Combiner Panel | AH3 | LOCKOUT_86 | DI | Lockout relay 86 operated |  |  | RLY-AH3 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH3.CMD_RESET | 11kV GIS Combiner Panel | AH3 | CMD_RESET | DO | Protection / lockout reset |  |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.I_L1 | 11kV GIS Combiner Panel | AH3 | I_L1 | AI | Current L1 | A |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.I_L2 | 11kV GIS Combiner Panel | AH3 | I_L2 | AI | Current L2 | A |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.I_L3 | 11kV GIS Combiner Panel | AH3 | I_L3 | AI | Current L3 | A |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.I_N | 11kV GIS Combiner Panel | AH3 | I_N | AI | Neutral / residual current | A |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.U_L12 | 11kV GIS Combiner Panel | AH3 | U_L12 | AI | Voltage L12 | kV |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.U_L23 | 11kV GIS Combiner Panel | AH3 | U_L23 | AI | Voltage L23 | kV |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.U_L31 | 11kV GIS Combiner Panel | AH3 | U_L31 | AI | Voltage L31 | kV |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.P | 11kV GIS Combiner Panel | AH3 | P | AI | Active power | kW |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.Q | 11kV GIS Combiner Panel | AH3 | Q | AI | Reactive power | kvar |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.S | 11kV GIS Combiner Panel | AH3 | S | AI | Apparent power | kVA |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.PF | 11kV GIS Combiner Panel | AH3 | PF | AI | Power factor |  |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.F | 11kV GIS Combiner Panel | AH3 | F | AI | Frequency | Hz |  | RLY-AH3 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.AH3.E_IMP | 11kV GIS Combiner Panel | AH3 | E_IMP | AI | Active energy import | MWh |  | RLY-AH3 | IEC 61850 MMS
GIS.AH3.E_EXP | 11kV GIS Combiner Panel | AH3 | E_EXP | AI | Active energy export | MWh |  | RLY-AH3 | IEC 61850 MMS
GIS.AH4.CB_CLOSED | 11kV GIS Combiner Panel | AH4 | CB_CLOSED | DI | QF14 VCB closed |  |  | RLY-AH4 | IEC 61850 MMS | GISAH4CTRL/XCBR1.Pos.stVal
GIS.AH4.CB_OPEN | 11kV GIS Combiner Panel | AH4 | CB_OPEN | DI | QF14 VCB open |  |  | RLY-AH4 | IEC 61850 MMS | GISAH4CTRL/XCBR1.Pos.stVal
GIS.AH4.CB_TRIPPED | 11kV GIS Combiner Panel | AH4 | CB_TRIPPED | DI | QF14 VCB tripped (protection) |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH4.CB_SPRING | 11kV GIS Combiner Panel | AH4 | CB_SPRING | DI | QF14 VCB spring charged |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 0 | 3
GIS.AH4.TCS_FAIL | 11kV GIS Combiner Panel | AH4 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH4.LR_REMOTE | 11kV GIS Combiner Panel | AH4 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 0 | 4
GIS.AH4.CMD_OPEN | 11kV GIS Combiner Panel | AH4 | CMD_OPEN | DO | QF14 VCB open command |  |  | RLY-AH4 | IEC 61850 MMS | GISAH4CTRL/XCBR1.Pos.Oper
GIS.AH4.CMD_CLOSE | 11kV GIS Combiner Panel | AH4 | CMD_CLOSE | DO | QF14 VCB close command |  |  | RLY-AH4 | IEC 61850 MMS | GISAH4CTRL/XCBR1.Pos.Oper
GIS.AH4.DS_CLOSED | 11kV GIS Combiner Panel | AH4 | DS_CLOSED | DI | QL14 3-position switch - closed (line) |  |  | RLY-AH4 | IEC 61850 MMS | GISAH4CTRL/XSWI1.Pos.stVal
GIS.AH4.ES_EARTHED | 11kV GIS Combiner Panel | AH4 | ES_EARTHED | DI | QL14 3-position switch - earthed |  |  | RLY-AH4 | IEC 61850 MMS | GISAH4CTRL/XSWI2.Pos.stVal
GIS.AH4.VPIS | 11kV GIS Combiner Panel | AH4 | VPIS | DI | Voltage presence indicator (DXN-12Q) |  |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.SF6_LOW | 11kV GIS Combiner Panel | AH4 | SF6_LOW | DI | SF6 gas pressure low (alarm) |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH4.SF6_LOLO | 11kV GIS Combiner Panel | AH4 | SF6_LOLO | DI | SF6 gas pressure low-low (block) |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH4.RLY_HEALTHY | 11kV GIS Combiner Panel | AH4 | RLY_HEALTHY | DI | Protection relay healthy (watchdog) |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 0 | 1
GIS.AH4.MCB_TRIP | 11kV GIS Combiner Panel | AH4 | MCB_TRIP | DI | Aux supply MCB tripped |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH4.SPD_OPER | 11kV GIS Combiner Panel | AH4 | SPD_OPER | DI | Surge arrester (HY5WS-17/50) operated |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 3
GIS.AH4.PROT_50 | 11kV GIS Combiner Panel | AH4 | PROT_50 | DI | Trip 50/51 phase overcurrent |  |  | RLY-AH4 | IEC 61850 MMS | GISAH4PROT/PTOC1.Op | On state = 1 | 1
GIS.AH4.PROT_50N | 11kV GIS Combiner Panel | AH4 | PROT_50N | DI | Trip 50N/51N earth fault |  |  | RLY-AH4 | IEC 61850 MMS | GISAH4PROT/PTOC2.Op | On state = 1 | 1
GIS.AH4.PROT_50G | 11kV GIS Combiner Panel | AH4 | PROT_50G | DI | Trip 51G sensitive earth fault (ZSCT) |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH4.PROT_46 | 11kV GIS Combiner Panel | AH4 | PROT_46 | DI | Trip 46 negative sequence / broken conductor |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH4.LOCKOUT_86 | 11kV GIS Combiner Panel | AH4 | LOCKOUT_86 | DI | Lockout relay 86 operated |  |  | RLY-AH4 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH4.CMD_RESET | 11kV GIS Combiner Panel | AH4 | CMD_RESET | DO | Protection / lockout reset |  |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.I_L1 | 11kV GIS Combiner Panel | AH4 | I_L1 | AI | Current L1 | A |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.I_L2 | 11kV GIS Combiner Panel | AH4 | I_L2 | AI | Current L2 | A |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.I_L3 | 11kV GIS Combiner Panel | AH4 | I_L3 | AI | Current L3 | A |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.I_N | 11kV GIS Combiner Panel | AH4 | I_N | AI | Neutral / residual current | A |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.U_L12 | 11kV GIS Combiner Panel | AH4 | U_L12 | AI | Voltage L12 | kV |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.U_L23 | 11kV GIS Combiner Panel | AH4 | U_L23 | AI | Voltage L23 | kV |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.U_L31 | 11kV GIS Combiner Panel | AH4 | U_L31 | AI | Voltage L31 | kV |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.P | 11kV GIS Combiner Panel | AH4 | P | AI | Active power | kW |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.Q | 11kV GIS Combiner Panel | AH4 | Q | AI | Reactive power | kvar |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.S | 11kV GIS Combiner Panel | AH4 | S | AI | Apparent power | kVA |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.PF | 11kV GIS Combiner Panel | AH4 | PF | AI | Power factor |  |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.F | 11kV GIS Combiner Panel | AH4 | F | AI | Frequency | Hz |  | RLY-AH4 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.AH4.E_IMP | 11kV GIS Combiner Panel | AH4 | E_IMP | AI | Active energy import | MWh |  | RLY-AH4 | IEC 61850 MMS
GIS.AH4.E_EXP | 11kV GIS Combiner Panel | AH4 | E_EXP | AI | Active energy export | MWh |  | RLY-AH4 | IEC 61850 MMS
GIS.AH5.CB_CLOSED | 11kV GIS Combiner Panel | AH5 | CB_CLOSED | DI | QF15 VCB closed |  |  | RLY-AH5 | IEC 61850 MMS | GISAH5CTRL/XCBR1.Pos.stVal
GIS.AH5.CB_OPEN | 11kV GIS Combiner Panel | AH5 | CB_OPEN | DI | QF15 VCB open |  |  | RLY-AH5 | IEC 61850 MMS | GISAH5CTRL/XCBR1.Pos.stVal
GIS.AH5.CB_TRIPPED | 11kV GIS Combiner Panel | AH5 | CB_TRIPPED | DI | QF15 VCB tripped (protection) |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH5.CB_SPRING | 11kV GIS Combiner Panel | AH5 | CB_SPRING | DI | QF15 VCB spring charged |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 0 | 3
GIS.AH5.TCS_FAIL | 11kV GIS Combiner Panel | AH5 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH5.LR_REMOTE | 11kV GIS Combiner Panel | AH5 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 0 | 4
GIS.AH5.CMD_OPEN | 11kV GIS Combiner Panel | AH5 | CMD_OPEN | DO | QF15 VCB open command |  |  | RLY-AH5 | IEC 61850 MMS | GISAH5CTRL/XCBR1.Pos.Oper
GIS.AH5.CMD_CLOSE | 11kV GIS Combiner Panel | AH5 | CMD_CLOSE | DO | QF15 VCB close command |  |  | RLY-AH5 | IEC 61850 MMS | GISAH5CTRL/XCBR1.Pos.Oper
GIS.AH5.DS_CLOSED | 11kV GIS Combiner Panel | AH5 | DS_CLOSED | DI | QL15 3-position switch - closed (line) |  |  | RLY-AH5 | IEC 61850 MMS | GISAH5CTRL/XSWI1.Pos.stVal
GIS.AH5.ES_EARTHED | 11kV GIS Combiner Panel | AH5 | ES_EARTHED | DI | QL15 3-position switch - earthed |  |  | RLY-AH5 | IEC 61850 MMS | GISAH5CTRL/XSWI2.Pos.stVal
GIS.AH5.VPIS | 11kV GIS Combiner Panel | AH5 | VPIS | DI | Voltage presence indicator (DXN-12Q) |  |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.SF6_LOW | 11kV GIS Combiner Panel | AH5 | SF6_LOW | DI | SF6 gas pressure low (alarm) |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH5.SF6_LOLO | 11kV GIS Combiner Panel | AH5 | SF6_LOLO | DI | SF6 gas pressure low-low (block) |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH5.RLY_HEALTHY | 11kV GIS Combiner Panel | AH5 | RLY_HEALTHY | DI | Protection relay healthy (watchdog) |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 0 | 1
GIS.AH5.MCB_TRIP | 11kV GIS Combiner Panel | AH5 | MCB_TRIP | DI | Aux supply MCB tripped |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH5.PROT_50 | 11kV GIS Combiner Panel | AH5 | PROT_50 | DI | Trip 50/51 phase overcurrent |  |  | RLY-AH5 | IEC 61850 MMS | GISAH5PROT/PTOC1.Op | On state = 1 | 1
GIS.AH5.PROT_50N | 11kV GIS Combiner Panel | AH5 | PROT_50N | DI | Trip 50N/51N earth fault |  |  | RLY-AH5 | IEC 61850 MMS | GISAH5PROT/PTOC2.Op | On state = 1 | 1
GIS.AH5.PROT_46 | 11kV GIS Combiner Panel | AH5 | PROT_46 | DI | Trip 46 negative sequence / broken conductor |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH5.LOCKOUT_86 | 11kV GIS Combiner Panel | AH5 | LOCKOUT_86 | DI | Lockout relay 86 operated |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH5.CMD_RESET | 11kV GIS Combiner Panel | AH5 | CMD_RESET | DO | Protection / lockout reset |  |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.I_L1 | 11kV GIS Combiner Panel | AH5 | I_L1 | AI | Current L1 | A |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.I_L2 | 11kV GIS Combiner Panel | AH5 | I_L2 | AI | Current L2 | A |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.I_L3 | 11kV GIS Combiner Panel | AH5 | I_L3 | AI | Current L3 | A |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.I_N | 11kV GIS Combiner Panel | AH5 | I_N | AI | Neutral / residual current | A |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.U_L12 | 11kV GIS Combiner Panel | AH5 | U_L12 | AI | Voltage L12 | kV |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.U_L23 | 11kV GIS Combiner Panel | AH5 | U_L23 | AI | Voltage L23 | kV |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.U_L31 | 11kV GIS Combiner Panel | AH5 | U_L31 | AI | Voltage L31 | kV |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.P | 11kV GIS Combiner Panel | AH5 | P | AI | Active power | kW |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.Q | 11kV GIS Combiner Panel | AH5 | Q | AI | Reactive power | kvar |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.S | 11kV GIS Combiner Panel | AH5 | S | AI | Apparent power | kVA |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.PF | 11kV GIS Combiner Panel | AH5 | PF | AI | Power factor |  |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.F | 11kV GIS Combiner Panel | AH5 | F | AI | Frequency | Hz |  | RLY-AH5 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.AH5.E_IMP | 11kV GIS Combiner Panel | AH5 | E_IMP | AI | Active energy import | MWh |  | RLY-AH5 | IEC 61850 MMS
GIS.AH5.E_EXP | 11kV GIS Combiner Panel | AH5 | E_EXP | AI | Active energy export | MWh |  | RLY-AH5 | IEC 61850 MMS
GIS.AH6.CB_CLOSED | 11kV GIS Combiner Panel | AH6 | CB_CLOSED | DI | QF16 VCB closed |  |  | RLY-AH6 | IEC 61850 MMS | GISAH6CTRL/XCBR1.Pos.stVal
GIS.AH6.CB_OPEN | 11kV GIS Combiner Panel | AH6 | CB_OPEN | DI | QF16 VCB open |  |  | RLY-AH6 | IEC 61850 MMS | GISAH6CTRL/XCBR1.Pos.stVal
GIS.AH6.CB_TRIPPED | 11kV GIS Combiner Panel | AH6 | CB_TRIPPED | DI | QF16 VCB tripped (protection) |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH6.CB_SPRING | 11kV GIS Combiner Panel | AH6 | CB_SPRING | DI | QF16 VCB spring charged |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 0 | 3
GIS.AH6.TCS_FAIL | 11kV GIS Combiner Panel | AH6 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH6.LR_REMOTE | 11kV GIS Combiner Panel | AH6 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 0 | 4
GIS.AH6.CMD_OPEN | 11kV GIS Combiner Panel | AH6 | CMD_OPEN | DO | QF16 VCB open command |  |  | RLY-AH6 | IEC 61850 MMS | GISAH6CTRL/XCBR1.Pos.Oper
GIS.AH6.CMD_CLOSE | 11kV GIS Combiner Panel | AH6 | CMD_CLOSE | DO | QF16 VCB close command |  |  | RLY-AH6 | IEC 61850 MMS | GISAH6CTRL/XCBR1.Pos.Oper
GIS.AH6.DS_CLOSED | 11kV GIS Combiner Panel | AH6 | DS_CLOSED | DI | QL16 3-position switch - closed (line) |  |  | RLY-AH6 | IEC 61850 MMS | GISAH6CTRL/XSWI1.Pos.stVal
GIS.AH6.ES_EARTHED | 11kV GIS Combiner Panel | AH6 | ES_EARTHED | DI | QL16 3-position switch - earthed |  |  | RLY-AH6 | IEC 61850 MMS | GISAH6CTRL/XSWI2.Pos.stVal
GIS.AH6.VPIS | 11kV GIS Combiner Panel | AH6 | VPIS | DI | Voltage presence indicator (DXN-12Q) |  |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.SF6_LOW | 11kV GIS Combiner Panel | AH6 | SF6_LOW | DI | SF6 gas pressure low (alarm) |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH6.SF6_LOLO | 11kV GIS Combiner Panel | AH6 | SF6_LOLO | DI | SF6 gas pressure low-low (block) |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH6.RLY_HEALTHY | 11kV GIS Combiner Panel | AH6 | RLY_HEALTHY | DI | Protection relay healthy (watchdog) |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 0 | 1
GIS.AH6.MCB_TRIP | 11kV GIS Combiner Panel | AH6 | MCB_TRIP | DI | Aux supply MCB tripped |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH6.SPD_OPER | 11kV GIS Combiner Panel | AH6 | SPD_OPER | DI | Surge arrester (HY5WS-17/50) operated |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 3
GIS.AH6.PROT_50 | 11kV GIS Combiner Panel | AH6 | PROT_50 | DI | Trip 50/51 phase overcurrent |  |  | RLY-AH6 | IEC 61850 MMS | GISAH6PROT/PTOC1.Op | On state = 1 | 1
GIS.AH6.PROT_50N | 11kV GIS Combiner Panel | AH6 | PROT_50N | DI | Trip 50N/51N earth fault |  |  | RLY-AH6 | IEC 61850 MMS | GISAH6PROT/PTOC2.Op | On state = 1 | 1
GIS.AH6.PROT_50G | 11kV GIS Combiner Panel | AH6 | PROT_50G | DI | Trip 51G sensitive earth fault (ZSCT) |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH6.PROT_46 | 11kV GIS Combiner Panel | AH6 | PROT_46 | DI | Trip 46 negative sequence / broken conductor |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH6.LOCKOUT_86 | 11kV GIS Combiner Panel | AH6 | LOCKOUT_86 | DI | Lockout relay 86 operated |  |  | RLY-AH6 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH6.CMD_RESET | 11kV GIS Combiner Panel | AH6 | CMD_RESET | DO | Protection / lockout reset |  |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.I_L1 | 11kV GIS Combiner Panel | AH6 | I_L1 | AI | Current L1 | A |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.I_L2 | 11kV GIS Combiner Panel | AH6 | I_L2 | AI | Current L2 | A |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.I_L3 | 11kV GIS Combiner Panel | AH6 | I_L3 | AI | Current L3 | A |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.I_N | 11kV GIS Combiner Panel | AH6 | I_N | AI | Neutral / residual current | A |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.U_L12 | 11kV GIS Combiner Panel | AH6 | U_L12 | AI | Voltage L12 | kV |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.U_L23 | 11kV GIS Combiner Panel | AH6 | U_L23 | AI | Voltage L23 | kV |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.U_L31 | 11kV GIS Combiner Panel | AH6 | U_L31 | AI | Voltage L31 | kV |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.P | 11kV GIS Combiner Panel | AH6 | P | AI | Active power | kW |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.Q | 11kV GIS Combiner Panel | AH6 | Q | AI | Reactive power | kvar |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.S | 11kV GIS Combiner Panel | AH6 | S | AI | Apparent power | kVA |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.PF | 11kV GIS Combiner Panel | AH6 | PF | AI | Power factor |  |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.F | 11kV GIS Combiner Panel | AH6 | F | AI | Frequency | Hz |  | RLY-AH6 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.AH6.E_IMP | 11kV GIS Combiner Panel | AH6 | E_IMP | AI | Active energy import | MWh |  | RLY-AH6 | IEC 61850 MMS
GIS.AH6.E_EXP | 11kV GIS Combiner Panel | AH6 | E_EXP | AI | Active energy export | MWh |  | RLY-AH6 | IEC 61850 MMS
GIS.AH7.CB_CLOSED | 11kV GIS Combiner Panel | AH7 | CB_CLOSED | DI | QF17 VCB closed |  |  | RLY-AH7 | IEC 61850 MMS | GISAH7CTRL/XCBR1.Pos.stVal
GIS.AH7.CB_OPEN | 11kV GIS Combiner Panel | AH7 | CB_OPEN | DI | QF17 VCB open |  |  | RLY-AH7 | IEC 61850 MMS | GISAH7CTRL/XCBR1.Pos.stVal
GIS.AH7.CB_TRIPPED | 11kV GIS Combiner Panel | AH7 | CB_TRIPPED | DI | QF17 VCB tripped (protection) |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH7.CB_SPRING | 11kV GIS Combiner Panel | AH7 | CB_SPRING | DI | QF17 VCB spring charged |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 0 | 3
GIS.AH7.TCS_FAIL | 11kV GIS Combiner Panel | AH7 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH7.LR_REMOTE | 11kV GIS Combiner Panel | AH7 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 0 | 4
GIS.AH7.CMD_OPEN | 11kV GIS Combiner Panel | AH7 | CMD_OPEN | DO | QF17 VCB open command |  |  | RLY-AH7 | IEC 61850 MMS | GISAH7CTRL/XCBR1.Pos.Oper
GIS.AH7.CMD_CLOSE | 11kV GIS Combiner Panel | AH7 | CMD_CLOSE | DO | QF17 VCB close command |  |  | RLY-AH7 | IEC 61850 MMS | GISAH7CTRL/XCBR1.Pos.Oper
GIS.AH7.DS_CLOSED | 11kV GIS Combiner Panel | AH7 | DS_CLOSED | DI | QL17 3-position switch - closed (line) |  |  | RLY-AH7 | IEC 61850 MMS | GISAH7CTRL/XSWI1.Pos.stVal
GIS.AH7.ES_EARTHED | 11kV GIS Combiner Panel | AH7 | ES_EARTHED | DI | QL17 3-position switch - earthed |  |  | RLY-AH7 | IEC 61850 MMS | GISAH7CTRL/XSWI2.Pos.stVal
GIS.AH7.VPIS | 11kV GIS Combiner Panel | AH7 | VPIS | DI | Voltage presence indicator (DXN-12Q) |  |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.SF6_LOW | 11kV GIS Combiner Panel | AH7 | SF6_LOW | DI | SF6 gas pressure low (alarm) |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH7.SF6_LOLO | 11kV GIS Combiner Panel | AH7 | SF6_LOLO | DI | SF6 gas pressure low-low (block) |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH7.RLY_HEALTHY | 11kV GIS Combiner Panel | AH7 | RLY_HEALTHY | DI | Protection relay healthy (watchdog) |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 0 | 1
GIS.AH7.MCB_TRIP | 11kV GIS Combiner Panel | AH7 | MCB_TRIP | DI | Aux supply MCB tripped |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH7.SPD_OPER | 11kV GIS Combiner Panel | AH7 | SPD_OPER | DI | Surge arrester (HY5WS-17/50) operated |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 3
GIS.AH7.PROT_50 | 11kV GIS Combiner Panel | AH7 | PROT_50 | DI | Trip 50/51 phase overcurrent |  |  | RLY-AH7 | IEC 61850 MMS | GISAH7PROT/PTOC1.Op | On state = 1 | 1
GIS.AH7.PROT_50N | 11kV GIS Combiner Panel | AH7 | PROT_50N | DI | Trip 50N/51N earth fault |  |  | RLY-AH7 | IEC 61850 MMS | GISAH7PROT/PTOC2.Op | On state = 1 | 1
GIS.AH7.PROT_50G | 11kV GIS Combiner Panel | AH7 | PROT_50G | DI | Trip 51G sensitive earth fault (ZSCT) |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH7.PROT_46 | 11kV GIS Combiner Panel | AH7 | PROT_46 | DI | Trip 46 negative sequence / broken conductor |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH7.LOCKOUT_86 | 11kV GIS Combiner Panel | AH7 | LOCKOUT_86 | DI | Lockout relay 86 operated |  |  | RLY-AH7 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH7.CMD_RESET | 11kV GIS Combiner Panel | AH7 | CMD_RESET | DO | Protection / lockout reset |  |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.I_L1 | 11kV GIS Combiner Panel | AH7 | I_L1 | AI | Current L1 | A |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.I_L2 | 11kV GIS Combiner Panel | AH7 | I_L2 | AI | Current L2 | A |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.I_L3 | 11kV GIS Combiner Panel | AH7 | I_L3 | AI | Current L3 | A |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.I_N | 11kV GIS Combiner Panel | AH7 | I_N | AI | Neutral / residual current | A |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.U_L12 | 11kV GIS Combiner Panel | AH7 | U_L12 | AI | Voltage L12 | kV |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.U_L23 | 11kV GIS Combiner Panel | AH7 | U_L23 | AI | Voltage L23 | kV |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.U_L31 | 11kV GIS Combiner Panel | AH7 | U_L31 | AI | Voltage L31 | kV |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.P | 11kV GIS Combiner Panel | AH7 | P | AI | Active power | kW |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.Q | 11kV GIS Combiner Panel | AH7 | Q | AI | Reactive power | kvar |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.S | 11kV GIS Combiner Panel | AH7 | S | AI | Apparent power | kVA |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.PF | 11kV GIS Combiner Panel | AH7 | PF | AI | Power factor |  |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.F | 11kV GIS Combiner Panel | AH7 | F | AI | Frequency | Hz |  | RLY-AH7 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.AH7.E_IMP | 11kV GIS Combiner Panel | AH7 | E_IMP | AI | Active energy import | MWh |  | RLY-AH7 | IEC 61850 MMS
GIS.AH7.E_EXP | 11kV GIS Combiner Panel | AH7 | E_EXP | AI | Active energy export | MWh |  | RLY-AH7 | IEC 61850 MMS
GIS.AH8.CB_CLOSED | 11kV GIS Combiner Panel | AH8 | CB_CLOSED | DI | QF18 VCB closed |  |  | RLY-AH8 | IEC 61850 MMS | GISAH8CTRL/XCBR1.Pos.stVal
GIS.AH8.CB_OPEN | 11kV GIS Combiner Panel | AH8 | CB_OPEN | DI | QF18 VCB open |  |  | RLY-AH8 | IEC 61850 MMS | GISAH8CTRL/XCBR1.Pos.stVal
GIS.AH8.CB_TRIPPED | 11kV GIS Combiner Panel | AH8 | CB_TRIPPED | DI | QF18 VCB tripped (protection) |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH8.CB_SPRING | 11kV GIS Combiner Panel | AH8 | CB_SPRING | DI | QF18 VCB spring charged |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 0 | 3
GIS.AH8.TCS_FAIL | 11kV GIS Combiner Panel | AH8 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH8.LR_REMOTE | 11kV GIS Combiner Panel | AH8 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 0 | 4
GIS.AH8.CMD_OPEN | 11kV GIS Combiner Panel | AH8 | CMD_OPEN | DO | QF18 VCB open command |  |  | RLY-AH8 | IEC 61850 MMS | GISAH8CTRL/XCBR1.Pos.Oper
GIS.AH8.CMD_CLOSE | 11kV GIS Combiner Panel | AH8 | CMD_CLOSE | DO | QF18 VCB close command |  |  | RLY-AH8 | IEC 61850 MMS | GISAH8CTRL/XCBR1.Pos.Oper
GIS.AH8.DS_CLOSED | 11kV GIS Combiner Panel | AH8 | DS_CLOSED | DI | QL18 3-position switch - closed (line) |  |  | RLY-AH8 | IEC 61850 MMS | GISAH8CTRL/XSWI1.Pos.stVal
GIS.AH8.ES_EARTHED | 11kV GIS Combiner Panel | AH8 | ES_EARTHED | DI | QL18 3-position switch - earthed |  |  | RLY-AH8 | IEC 61850 MMS | GISAH8CTRL/XSWI2.Pos.stVal
GIS.AH8.VPIS | 11kV GIS Combiner Panel | AH8 | VPIS | DI | Voltage presence indicator (DXN-12Q) |  |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.SF6_LOW | 11kV GIS Combiner Panel | AH8 | SF6_LOW | DI | SF6 gas pressure low (alarm) |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH8.SF6_LOLO | 11kV GIS Combiner Panel | AH8 | SF6_LOLO | DI | SF6 gas pressure low-low (block) |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH8.RLY_HEALTHY | 11kV GIS Combiner Panel | AH8 | RLY_HEALTHY | DI | Protection relay healthy (watchdog) |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 0 | 1
GIS.AH8.MCB_TRIP | 11kV GIS Combiner Panel | AH8 | MCB_TRIP | DI | Aux supply MCB tripped |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 2
GIS.AH8.SPD_OPER | 11kV GIS Combiner Panel | AH8 | SPD_OPER | DI | Surge arrester (HY5WS-17/50) operated |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 3
GIS.AH8.PROT_50 | 11kV GIS Combiner Panel | AH8 | PROT_50 | DI | Trip 50/51 phase overcurrent |  |  | RLY-AH8 | IEC 61850 MMS | GISAH8PROT/PTOC1.Op | On state = 1 | 1
GIS.AH8.PROT_50N | 11kV GIS Combiner Panel | AH8 | PROT_50N | DI | Trip 50N/51N earth fault |  |  | RLY-AH8 | IEC 61850 MMS | GISAH8PROT/PTOC2.Op | On state = 1 | 1
GIS.AH8.PROT_50G | 11kV GIS Combiner Panel | AH8 | PROT_50G | DI | Trip 51G sensitive earth fault (ZSCT) |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH8.PROT_46 | 11kV GIS Combiner Panel | AH8 | PROT_46 | DI | Trip 46 negative sequence / broken conductor |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH8.PROT_64 | 11kV GIS Combiner Panel | AH8 | PROT_64 | DI | NER over-temperature / standby EF (64/51NS) |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH8.LOCKOUT_86 | 11kV GIS Combiner Panel | AH8 | LOCKOUT_86 | DI | Lockout relay 86 operated |  |  | RLY-AH8 | IEC 61850 MMS |  | On state = 1 | 1
GIS.AH8.CMD_RESET | 11kV GIS Combiner Panel | AH8 | CMD_RESET | DO | Protection / lockout reset |  |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.I_L1 | 11kV GIS Combiner Panel | AH8 | I_L1 | AI | Current L1 | A |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.I_L2 | 11kV GIS Combiner Panel | AH8 | I_L2 | AI | Current L2 | A |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.I_L3 | 11kV GIS Combiner Panel | AH8 | I_L3 | AI | Current L3 | A |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.I_N | 11kV GIS Combiner Panel | AH8 | I_N | AI | Neutral / residual current | A |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.U_L12 | 11kV GIS Combiner Panel | AH8 | U_L12 | AI | Voltage L12 | kV |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.U_L23 | 11kV GIS Combiner Panel | AH8 | U_L23 | AI | Voltage L23 | kV |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.U_L31 | 11kV GIS Combiner Panel | AH8 | U_L31 | AI | Voltage L31 | kV |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.P | 11kV GIS Combiner Panel | AH8 | P | AI | Active power | kW |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.Q | 11kV GIS Combiner Panel | AH8 | Q | AI | Reactive power | kvar |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.S | 11kV GIS Combiner Panel | AH8 | S | AI | Apparent power | kVA |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.PF | 11kV GIS Combiner Panel | AH8 | PF | AI | Power factor |  |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.F | 11kV GIS Combiner Panel | AH8 | F | AI | Frequency | Hz |  | RLY-AH8 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.AH8.E_IMP | 11kV GIS Combiner Panel | AH8 | E_IMP | AI | Active energy import | MWh |  | RLY-AH8 | IEC 61850 MMS
GIS.AH8.E_EXP | 11kV GIS Combiner Panel | AH8 | E_EXP | AI | Active energy export | MWh |  | RLY-AH8 | IEC 61850 MMS
GIS.BUS.U | 11kV GIS Combiner Panel | BUS | U | AI | 11kV busbar voltage | kV |  | RLY-AH3 | IEC 61850 MMS |  | Limits | 1/2 | 9.9 | 10.45 | 11.55 | 12.1
GIS.BUS.F | 11kV GIS Combiner Panel | BUS | F | AI | 11kV busbar frequency | Hz |  | RLY-AH3 | IEC 61850 MMS |  | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
GIS.BUS.LIVE | 11kV GIS Combiner Panel | BUS | LIVE | DI | 11kV busbar energised |  |  | SCADA | Calculated |  | On state = 0 | 1
GIS.NECR.I_NER | 11kV GIS Combiner Panel | NECR | I_NER | AI | Neutral earthing resistor current (63.5Ω 100A 10s) | A |  | RLY-AH8 | IEC 61850 MMS |  | Limits | 1/2 |  |  | 10 | 50
GIS.NECR.T_NER | 11kV GIS Combiner Panel | NECR | T_NER | AI | NER resistor element temperature | °C |  | RLY-AH8 | IEC 61850 MMS |  | Limits | 1/2 |  |  | 300 | 400
GIS.DC.U_DC | 11kV GIS Combiner Panel | DC | U_DC | AI | 110VDC switchgear supply voltage | V |  | DC-CHG | Modbus TCP | 30002 | Limits | 1/2 | 95 | 102 | 125 | 130
GIS.DC.CHG_FAIL | 11kV GIS Combiner Panel | DC | CHG_FAIL | DI | 110VDC charger fail |  |  | DC-CHG | Modbus TCP | 10001 | On state = 1 | 2
GIS.DC.EARTH_FLT | 11kV GIS Combiner Panel | DC | EARTH_FLT | DI | 110VDC earth fault |  |  | DC-CHG | Modbus TCP | 10002 | On state = 1 | 3
GIS.ROOM.T_ROOM | 11kV GIS Combiner Panel | ROOM | T_ROOM | AI | GIS room temperature | °C |  | PLC-AUX | Modbus TCP | 30002 | Limits | 1/2 |  |  | 35 | 40
GIS.ROOM.DOOR | 11kV GIS Combiner Panel | ROOM | DOOR | DI | GIS room door open |  |  | PLC-AUX | Modbus TCP | 10001 | On state = 1 | 4
TX.DGTX.T_OIL | Transformers | DGTX | T_OIL | AI | DG Step-up TX oil / core temperature | °C |  | PLC-AUX | Modbus TCP | 30004 | Limits | 1/2 |  |  | 85 | 95
TX.DGTX.T_WDG | Transformers | DGTX | T_WDG | AI | DG Step-up TX winding temperature | °C |  | PLC-AUX | Modbus TCP | 30006 | Limits | 1/2 |  |  | 100 | 120
TX.DGTX.LOAD | Transformers | DGTX | LOAD | AI | DG Step-up TX loading | % |  | SCADA | Calculated |  | Limits | 1/2 |  |  | 90 | 110
TX.DGTX.TEMP_ALM | Transformers | DGTX | TEMP_ALM | DI | DG Step-up TX temperature alarm (1st stage) |  |  | PLC-AUX | Modbus TCP | 10002 | On state = 1 | 2
TX.DGTX.TEMP_TRIP | Transformers | DGTX | TEMP_TRIP | DI | DG Step-up TX temperature trip (2nd stage) |  |  | PLC-AUX | Modbus TCP | 10003 | On state = 1 | 1
TX.DGTX.BUCH_ALM | Transformers | DGTX | BUCH_ALM | DI | DG Step-up TX Buchholz / gas alarm |  |  | PLC-AUX | Modbus TCP | 10004 | On state = 1 | 2
TX.DGTX.BUCH_TRIP | Transformers | DGTX | BUCH_TRIP | DI | DG Step-up TX Buchholz / PRD trip |  |  | PLC-AUX | Modbus TCP | 10005 | On state = 1 | 1
TX.DGTX.OIL_LOW | Transformers | DGTX | OIL_LOW | DI | DG Step-up TX oil level low |  |  | PLC-AUX | Modbus TCP | 10006 | On state = 1 | 3
TX.PVTX.T_OIL | Transformers | PVTX | T_OIL | AI | PV Inverter TX oil / core temperature | °C |  | PLC-AUX | Modbus TCP | 30008 | Limits | 1/2 |  |  | 85 | 95
TX.PVTX.T_WDG | Transformers | PVTX | T_WDG | AI | PV Inverter TX winding temperature | °C |  | PLC-AUX | Modbus TCP | 30010 | Limits | 1/2 |  |  | 100 | 120
TX.PVTX.LOAD | Transformers | PVTX | LOAD | AI | PV Inverter TX loading | % |  | SCADA | Calculated |  | Limits | 1/2 |  |  | 90 | 110
TX.PVTX.TEMP_ALM | Transformers | PVTX | TEMP_ALM | DI | PV Inverter TX temperature alarm (1st stage) |  |  | PLC-AUX | Modbus TCP | 10007 | On state = 1 | 2
TX.PVTX.TEMP_TRIP | Transformers | PVTX | TEMP_TRIP | DI | PV Inverter TX temperature trip (2nd stage) |  |  | PLC-AUX | Modbus TCP | 10008 | On state = 1 | 1
TX.PVTX.BUCH_ALM | Transformers | PVTX | BUCH_ALM | DI | PV Inverter TX Buchholz / gas alarm |  |  | PLC-AUX | Modbus TCP | 10009 | On state = 1 | 2
TX.PVTX.BUCH_TRIP | Transformers | PVTX | BUCH_TRIP | DI | PV Inverter TX Buchholz / PRD trip |  |  | PLC-AUX | Modbus TCP | 10010 | On state = 1 | 1
TX.PVTX.OIL_LOW | Transformers | PVTX | OIL_LOW | DI | PV Inverter TX oil level low |  |  | PLC-AUX | Modbus TCP | 10011 | On state = 1 | 3
TX.BESSTX.T_OIL | Transformers | BESSTX | T_OIL | AI | BESS TX oil / core temperature | °C |  | PLC-AUX | Modbus TCP | 30012 | Limits | 1/2 |  |  | 85 | 95
TX.BESSTX.T_WDG | Transformers | BESSTX | T_WDG | AI | BESS TX winding temperature | °C |  | PLC-AUX | Modbus TCP | 30014 | Limits | 1/2 |  |  | 100 | 120
TX.BESSTX.LOAD | Transformers | BESSTX | LOAD | AI | BESS TX loading | % |  | SCADA | Calculated |  | Limits | 1/2 |  |  | 90 | 110
TX.BESSTX.TEMP_ALM | Transformers | BESSTX | TEMP_ALM | DI | BESS TX temperature alarm (1st stage) |  |  | PLC-AUX | Modbus TCP | 10012 | On state = 1 | 2
TX.BESSTX.TEMP_TRIP | Transformers | BESSTX | TEMP_TRIP | DI | BESS TX temperature trip (2nd stage) |  |  | PLC-AUX | Modbus TCP | 10013 | On state = 1 | 1
TX.BESSTX.BUCH_ALM | Transformers | BESSTX | BUCH_ALM | DI | BESS TX Buchholz / gas alarm |  |  | PLC-AUX | Modbus TCP | 10014 | On state = 1 | 2
TX.BESSTX.BUCH_TRIP | Transformers | BESSTX | BUCH_TRIP | DI | BESS TX Buchholz / PRD trip |  |  | PLC-AUX | Modbus TCP | 10015 | On state = 1 | 1
TX.BESSTX.OIL_LOW | Transformers | BESSTX | OIL_LOW | DI | BESS TX oil level low |  |  | PLC-AUX | Modbus TCP | 10016 | On state = 1 | 3
TX.PRESTX.T_OIL | Transformers | PRESTX | T_OIL | AI | President Office TX oil / core temperature | °C |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 30002 | Limits | 1/2 |  |  | 85 | 95
TX.PRESTX.T_WDG | Transformers | PRESTX | T_WDG | AI | President Office TX winding temperature | °C |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 30004 | Limits | 1/2 |  |  | 100 | 120
TX.PRESTX.LOAD | Transformers | PRESTX | LOAD | AI | President Office TX loading | % |  | SCADA | Calculated |  | Limits | 1/2 |  |  | 90 | 110
TX.PRESTX.TEMP_ALM | Transformers | PRESTX | TEMP_ALM | DI | President Office TX temperature alarm (1st stage) |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10001 | On state = 1 | 2
TX.PRESTX.TEMP_TRIP | Transformers | PRESTX | TEMP_TRIP | DI | President Office TX temperature trip (2nd stage) |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10002 | On state = 1 | 1
TX.PRESTX.BUCH_ALM | Transformers | PRESTX | BUCH_ALM | DI | President Office TX Buchholz / gas alarm |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10003 | On state = 1 | 2
TX.PRESTX.BUCH_TRIP | Transformers | PRESTX | BUCH_TRIP | DI | President Office TX Buchholz / PRD trip |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10004 | On state = 1 | 1
TX.PRESTX.OIL_LOW | Transformers | PRESTX | OIL_LOW | DI | President Office TX oil level low |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10005 | On state = 1 | 3
TX.PMTX.T_OIL | Transformers | PMTX | T_OIL | AI | Prime Minister Office TX oil / core temperature | °C |  | RLY-RMU_PM | Modbus TCP (via fibre) | 30002 | Limits | 1/2 |  |  | 85 | 95
TX.PMTX.T_WDG | Transformers | PMTX | T_WDG | AI | Prime Minister Office TX winding temperature | °C |  | RLY-RMU_PM | Modbus TCP (via fibre) | 30004 | Limits | 1/2 |  |  | 100 | 120
TX.PMTX.LOAD | Transformers | PMTX | LOAD | AI | Prime Minister Office TX loading | % |  | SCADA | Calculated |  | Limits | 1/2 |  |  | 90 | 110
TX.PMTX.TEMP_ALM | Transformers | PMTX | TEMP_ALM | DI | Prime Minister Office TX temperature alarm (1st stage) |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10001 | On state = 1 | 2
TX.PMTX.TEMP_TRIP | Transformers | PMTX | TEMP_TRIP | DI | Prime Minister Office TX temperature trip (2nd stage) |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10002 | On state = 1 | 1
TX.PMTX.BUCH_ALM | Transformers | PMTX | BUCH_ALM | DI | Prime Minister Office TX Buchholz / gas alarm |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10003 | On state = 1 | 2
TX.PMTX.BUCH_TRIP | Transformers | PMTX | BUCH_TRIP | DI | Prime Minister Office TX Buchholz / PRD trip |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10004 | On state = 1 | 1
TX.PMTX.OIL_LOW | Transformers | PMTX | OIL_LOW | DI | Prime Minister Office TX oil level low |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10005 | On state = 1 | 3
TX.AUXTX.T_OIL | Transformers | AUXTX | T_OIL | AI | Station Aux TX (SAT) oil / core temperature | °C |  | PLC-AUX | Modbus TCP | 30016 | Limits | 1/2 |  |  | 85 | 95
TX.AUXTX.T_WDG | Transformers | AUXTX | T_WDG | AI | Station Aux TX (SAT) winding temperature | °C |  | PLC-AUX | Modbus TCP | 30018 | Limits | 1/2 |  |  | 100 | 120
TX.AUXTX.LOAD | Transformers | AUXTX | LOAD | AI | Station Aux TX (SAT) loading | % |  | SCADA | Calculated |  | Limits | 1/2 |  |  | 90 | 110
TX.AUXTX.TEMP_ALM | Transformers | AUXTX | TEMP_ALM | DI | Station Aux TX (SAT) temperature alarm (1st stage) |  |  | PLC-AUX | Modbus TCP | 10017 | On state = 1 | 2
TX.AUXTX.TEMP_TRIP | Transformers | AUXTX | TEMP_TRIP | DI | Station Aux TX (SAT) temperature trip (2nd stage) |  |  | PLC-AUX | Modbus TCP | 10018 | On state = 1 | 1
TX.AUXTX.BUCH_ALM | Transformers | AUXTX | BUCH_ALM | DI | Station Aux TX (SAT) Buchholz / gas alarm |  |  | PLC-AUX | Modbus TCP | 10019 | On state = 1 | 2
TX.AUXTX.BUCH_TRIP | Transformers | AUXTX | BUCH_TRIP | DI | Station Aux TX (SAT) Buchholz / PRD trip |  |  | PLC-AUX | Modbus TCP | 10020 | On state = 1 | 1
TX.AUXTX.OIL_LOW | Transformers | AUXTX | OIL_LOW | DI | Station Aux TX (SAT) oil level low |  |  | PLC-AUX | Modbus TCP | 10021 | On state = 1 | 3
TX.AUXTX.FUSE_BLOWN | Transformers | AUXTX | FUSE_BLOWN | DI | SAT XRNT-3A HV fuse blown (striker) |  |  | RLY-AH5 | IEC 61850 MMS |  | On state = 1 | 1
RMU.RMU_PRES.AH1_CLOSED | Remote RMUs (President / P.M.) | RMU_PRES | AH1_CLOSED | DI | AH1 incomer QL11 closed |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10006
RMU.RMU_PRES.AH1_EARTHED | Remote RMUs (President / P.M.) | RMU_PRES | AH1_EARTHED | DI | AH1 incomer QL11 earthed |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10007
RMU.RMU_PRES.AH2_CLOSED | Remote RMUs (President / P.M.) | RMU_PRES | AH2_CLOSED | DI | AH2 outgoing QL12 closed |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10008
RMU.RMU_PRES.AH2_EARTHED | Remote RMUs (President / P.M.) | RMU_PRES | AH2_EARTHED | DI | AH2 outgoing QL12 earthed |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10009
RMU.RMU_PRES_AH3.CB_CLOSED | Remote RMUs (President / P.M.) | RMU_PRES_AH3 | CB_CLOSED | DI | AH3 QF11 VCB closed |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10010
RMU.RMU_PRES_AH3.CB_OPEN | Remote RMUs (President / P.M.) | RMU_PRES_AH3 | CB_OPEN | DI | AH3 QF11 VCB open |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10011
RMU.RMU_PRES_AH3.CB_TRIPPED | Remote RMUs (President / P.M.) | RMU_PRES_AH3 | CB_TRIPPED | DI | AH3 QF11 VCB tripped (protection) |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10012 | On state = 1 | 1
RMU.RMU_PRES_AH3.CB_SPRING | Remote RMUs (President / P.M.) | RMU_PRES_AH3 | CB_SPRING | DI | AH3 QF11 VCB spring charged |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10013 | On state = 0 | 3
RMU.RMU_PRES_AH3.TCS_FAIL | Remote RMUs (President / P.M.) | RMU_PRES_AH3 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10014 | On state = 1 | 2
RMU.RMU_PRES_AH3.LR_REMOTE | Remote RMUs (President / P.M.) | RMU_PRES_AH3 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10015 | On state = 0 | 4
RMU.RMU_PRES_AH3.CMD_OPEN | Remote RMUs (President / P.M.) | RMU_PRES_AH3 | CMD_OPEN | DO | AH3 QF11 VCB open command |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 1
RMU.RMU_PRES_AH3.CMD_CLOSE | Remote RMUs (President / P.M.) | RMU_PRES_AH3 | CMD_CLOSE | DO | AH3 QF11 VCB close command |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 2
RMU.RMU_PRES.QK11_EARTHED | Remote RMUs (President / P.M.) | RMU_PRES | QK11_EARTHED | DI | AH3 QK11 earth switch earthed |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10016
RMU.RMU_PRES.VPIS_DX11 | Remote RMUs (President / P.M.) | RMU_PRES | VPIS_DX11 | DI | DX11 voltage presence |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10017
RMU.RMU_PRES.VPIS_DX13 | Remote RMUs (President / P.M.) | RMU_PRES | VPIS_DX13 | DI | DX13 voltage presence |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10018
RMU.RMU_PRES.SF6_LOW | Remote RMUs (President / P.M.) | RMU_PRES | SF6_LOW | DI | SF6 gas pressure low |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10019 | On state = 1 | 2
RMU.RMU_PRES.RLY_HEALTHY | Remote RMUs (President / P.M.) | RMU_PRES | RLY_HEALTHY | DI | Zhuhai Strom ST260E relay healthy |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10020 | On state = 0 | 1
RMU.RMU_PRES.PROT_50 | Remote RMUs (President / P.M.) | RMU_PRES | PROT_50 | DI | ST260E trip 50/51 overcurrent |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10021 | On state = 1 | 1
RMU.RMU_PRES.PROT_50N | Remote RMUs (President / P.M.) | RMU_PRES | PROT_50N | DI | ST260E trip 50N/51N earth fault |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10022 | On state = 1 | 1
RMU.RMU_PRES.UPS_ONBATT | Remote RMUs (President / P.M.) | RMU_PRES | UPS_ONBATT | DI | RMU UPS 2kVA AC220V on battery |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10023 | On state = 1 | 3
RMU.RMU_PRES.UPS_FAIL | Remote RMUs (President / P.M.) | RMU_PRES | UPS_FAIL | DI | RMU UPS fault |  |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 10024 | On state = 1 | 2
RMU.RMU_PRES.COMM | Remote RMUs (President / P.M.) | RMU_PRES | COMM | DI | Fibre link to plant SCADA healthy |  |  | SW-RMU_PRES | SNMP |  | On state = 0 | 2
RMU.RMU_PRES.I_L1 | Remote RMUs (President / P.M.) | RMU_PRES | I_L1 | AI | AH3 current L1 | A |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 30006
RMU.RMU_PRES.I_L2 | Remote RMUs (President / P.M.) | RMU_PRES | I_L2 | AI | AH3 current L2 | A |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 30008
RMU.RMU_PRES.I_L3 | Remote RMUs (President / P.M.) | RMU_PRES | I_L3 | AI | AH3 current L3 | A |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 30010
RMU.RMU_PRES.I_N | Remote RMUs (President / P.M.) | RMU_PRES | I_N | AI | AH3 residual current | A |  | RLY-RMU_PRES | Modbus TCP (via fibre) | 30012
RMU.RMU_PM.AH1_CLOSED | Remote RMUs (President / P.M.) | RMU_PM | AH1_CLOSED | DI | AH1 incomer QL11 closed |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10006
RMU.RMU_PM.AH1_EARTHED | Remote RMUs (President / P.M.) | RMU_PM | AH1_EARTHED | DI | AH1 incomer QL11 earthed |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10007
RMU.RMU_PM.AH2_CLOSED | Remote RMUs (President / P.M.) | RMU_PM | AH2_CLOSED | DI | AH2 outgoing QL12 closed |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10008
RMU.RMU_PM.AH2_EARTHED | Remote RMUs (President / P.M.) | RMU_PM | AH2_EARTHED | DI | AH2 outgoing QL12 earthed |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10009
RMU.RMU_PM_AH3.CB_CLOSED | Remote RMUs (President / P.M.) | RMU_PM_AH3 | CB_CLOSED | DI | AH3 QF11 VCB closed |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10010
RMU.RMU_PM_AH3.CB_OPEN | Remote RMUs (President / P.M.) | RMU_PM_AH3 | CB_OPEN | DI | AH3 QF11 VCB open |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10011
RMU.RMU_PM_AH3.CB_TRIPPED | Remote RMUs (President / P.M.) | RMU_PM_AH3 | CB_TRIPPED | DI | AH3 QF11 VCB tripped (protection) |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10012 | On state = 1 | 1
RMU.RMU_PM_AH3.CB_SPRING | Remote RMUs (President / P.M.) | RMU_PM_AH3 | CB_SPRING | DI | AH3 QF11 VCB spring charged |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10013 | On state = 0 | 3
RMU.RMU_PM_AH3.TCS_FAIL | Remote RMUs (President / P.M.) | RMU_PM_AH3 | TCS_FAIL | DI | Trip circuit supervision fail |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10014 | On state = 1 | 2
RMU.RMU_PM_AH3.LR_REMOTE | Remote RMUs (President / P.M.) | RMU_PM_AH3 | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10015 | On state = 0 | 4
RMU.RMU_PM_AH3.CMD_OPEN | Remote RMUs (President / P.M.) | RMU_PM_AH3 | CMD_OPEN | DO | AH3 QF11 VCB open command |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 1
RMU.RMU_PM_AH3.CMD_CLOSE | Remote RMUs (President / P.M.) | RMU_PM_AH3 | CMD_CLOSE | DO | AH3 QF11 VCB close command |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 2
RMU.RMU_PM.QK11_EARTHED | Remote RMUs (President / P.M.) | RMU_PM | QK11_EARTHED | DI | AH3 QK11 earth switch earthed |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10016
RMU.RMU_PM.VPIS_DX11 | Remote RMUs (President / P.M.) | RMU_PM | VPIS_DX11 | DI | DX11 voltage presence |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10017
RMU.RMU_PM.VPIS_DX13 | Remote RMUs (President / P.M.) | RMU_PM | VPIS_DX13 | DI | DX13 voltage presence |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10018
RMU.RMU_PM.SF6_LOW | Remote RMUs (President / P.M.) | RMU_PM | SF6_LOW | DI | SF6 gas pressure low |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10019 | On state = 1 | 2
RMU.RMU_PM.RLY_HEALTHY | Remote RMUs (President / P.M.) | RMU_PM | RLY_HEALTHY | DI | Zhuhai Strom ST260E relay healthy |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10020 | On state = 0 | 1
RMU.RMU_PM.PROT_50 | Remote RMUs (President / P.M.) | RMU_PM | PROT_50 | DI | ST260E trip 50/51 overcurrent |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10021 | On state = 1 | 1
RMU.RMU_PM.PROT_50N | Remote RMUs (President / P.M.) | RMU_PM | PROT_50N | DI | ST260E trip 50N/51N earth fault |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10022 | On state = 1 | 1
RMU.RMU_PM.UPS_ONBATT | Remote RMUs (President / P.M.) | RMU_PM | UPS_ONBATT | DI | RMU UPS 2kVA AC220V on battery |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10023 | On state = 1 | 3
RMU.RMU_PM.UPS_FAIL | Remote RMUs (President / P.M.) | RMU_PM | UPS_FAIL | DI | RMU UPS fault |  |  | RLY-RMU_PM | Modbus TCP (via fibre) | 10024 | On state = 1 | 2
RMU.RMU_PM.COMM | Remote RMUs (President / P.M.) | RMU_PM | COMM | DI | Fibre link to plant SCADA healthy |  |  | SW-RMU_PM | SNMP |  | On state = 0 | 2
RMU.RMU_PM.I_L1 | Remote RMUs (President / P.M.) | RMU_PM | I_L1 | AI | AH3 current L1 | A |  | RLY-RMU_PM | Modbus TCP (via fibre) | 30006
RMU.RMU_PM.I_L2 | Remote RMUs (President / P.M.) | RMU_PM | I_L2 | AI | AH3 current L2 | A |  | RLY-RMU_PM | Modbus TCP (via fibre) | 30008
RMU.RMU_PM.I_L3 | Remote RMUs (President / P.M.) | RMU_PM | I_L3 | AI | AH3 current L3 | A |  | RLY-RMU_PM | Modbus TCP (via fibre) | 30010
RMU.RMU_PM.I_N | Remote RMUs (President / P.M.) | RMU_PM | I_N | AI | AH3 residual current | A |  | RLY-RMU_PM | Modbus TCP (via fibre) | 30012
LV.LVDB_PRES.CB_CLOSED | LV Distribution Boards | LVDB_PRES | CB_CLOSED | DI | Incomer ACB 1000A 31.5kA closed |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10001
LV.LVDB_PRES.CB_OPEN | LV Distribution Boards | LVDB_PRES | CB_OPEN | DI | Incomer ACB 1000A 31.5kA open |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10002
LV.LVDB_PRES.CB_TRIPPED | LV Distribution Boards | LVDB_PRES | CB_TRIPPED | DI | Incomer ACB 1000A 31.5kA tripped (protection) |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10003 | On state = 1 | 1
LV.LVDB_PRES.CB_SPRING | LV Distribution Boards | LVDB_PRES | CB_SPRING | DI | Incomer ACB 1000A 31.5kA spring charged |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10004 | On state = 0 | 3
LV.LVDB_PRES.CB_RACKED | LV Distribution Boards | LVDB_PRES | CB_RACKED | DI | Incomer ACB 1000A 31.5kA racked-in / service position |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10005
LV.LVDB_PRES.LR_REMOTE | LV Distribution Boards | LVDB_PRES | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10006 | On state = 0 | 4
LV.LVDB_PRES.CMD_OPEN | LV Distribution Boards | LVDB_PRES | CMD_OPEN | DO | Incomer ACB 1000A 31.5kA open command |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 1
LV.LVDB_PRES.CMD_CLOSE | LV Distribution Boards | LVDB_PRES | CMD_CLOSE | DO | Incomer ACB 1000A 31.5kA close command |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 2
LV.LVDB_PRES.I_L1 | LV Distribution Boards | LVDB_PRES | I_L1 | AI | Current L1 | A |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30002
LV.LVDB_PRES.I_L2 | LV Distribution Boards | LVDB_PRES | I_L2 | AI | Current L2 | A |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30004
LV.LVDB_PRES.I_L3 | LV Distribution Boards | LVDB_PRES | I_L3 | AI | Current L3 | A |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30006
LV.LVDB_PRES.I_N | LV Distribution Boards | LVDB_PRES | I_N | AI | Neutral / residual current | A |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30008
LV.LVDB_PRES.U_L12 | LV Distribution Boards | LVDB_PRES | U_L12 | AI | Voltage L12 | V |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30010
LV.LVDB_PRES.U_L23 | LV Distribution Boards | LVDB_PRES | U_L23 | AI | Voltage L23 | V |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30012
LV.LVDB_PRES.U_L31 | LV Distribution Boards | LVDB_PRES | U_L31 | AI | Voltage L31 | V |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30014
LV.LVDB_PRES.P | LV Distribution Boards | LVDB_PRES | P | AI | Active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30016
LV.LVDB_PRES.Q | LV Distribution Boards | LVDB_PRES | Q | AI | Reactive power | kvar |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30018
LV.LVDB_PRES.S | LV Distribution Boards | LVDB_PRES | S | AI | Apparent power | kVA |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30020
LV.LVDB_PRES.PF | LV Distribution Boards | LVDB_PRES | PF | AI | Power factor |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30022
LV.LVDB_PRES.F | LV Distribution Boards | LVDB_PRES | F | AI | Frequency | Hz |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30024 | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
LV.LVDB_PRES.E_IMP | LV Distribution Boards | LVDB_PRES | E_IMP | AI | Active energy import | MWh |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30026
LV.LVDB_PRES.E_EXP | LV Distribution Boards | LVDB_PRES | E_EXP | AI | Active energy export | MWh |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30028
LV.LVDB_PRES.THD_U | LV Distribution Boards | LVDB_PRES | THD_U | AI | Voltage THD | % |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30030 | Limits | 1/2 |  |  | 5 | 8
LV.LVDB_PRES.SPD_FAIL | LV Distribution Boards | LVDB_PRES | SPD_FAIL | DI | LV surge protective device failed |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10007 | On state = 1 | 3
LV.LVDB_PRES.W01_ON | LV Distribution Boards | LVDB_PRES | W01_ON | DI | Outgoing way 1 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10008
LV.LVDB_PRES.W01_TRIP | LV Distribution Boards | LVDB_PRES | W01_TRIP | DI | Outgoing way 1 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10009 | On state = 1 | 3
LV.LVDB_PRES.W01_P | LV Distribution Boards | LVDB_PRES | W01_P | AI | Outgoing way 1 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30032
LV.LVDB_PRES.W02_ON | LV Distribution Boards | LVDB_PRES | W02_ON | DI | Outgoing way 2 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10010
LV.LVDB_PRES.W02_TRIP | LV Distribution Boards | LVDB_PRES | W02_TRIP | DI | Outgoing way 2 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10011 | On state = 1 | 3
LV.LVDB_PRES.W02_P | LV Distribution Boards | LVDB_PRES | W02_P | AI | Outgoing way 2 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30034
LV.LVDB_PRES.W03_ON | LV Distribution Boards | LVDB_PRES | W03_ON | DI | Outgoing way 3 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10012
LV.LVDB_PRES.W03_TRIP | LV Distribution Boards | LVDB_PRES | W03_TRIP | DI | Outgoing way 3 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10013 | On state = 1 | 3
LV.LVDB_PRES.W03_P | LV Distribution Boards | LVDB_PRES | W03_P | AI | Outgoing way 3 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30036
LV.LVDB_PRES.W04_ON | LV Distribution Boards | LVDB_PRES | W04_ON | DI | Outgoing way 4 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10014
LV.LVDB_PRES.W04_TRIP | LV Distribution Boards | LVDB_PRES | W04_TRIP | DI | Outgoing way 4 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10015 | On state = 1 | 3
LV.LVDB_PRES.W04_P | LV Distribution Boards | LVDB_PRES | W04_P | AI | Outgoing way 4 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30038
LV.LVDB_PRES.W05_ON | LV Distribution Boards | LVDB_PRES | W05_ON | DI | Outgoing way 5 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10016
LV.LVDB_PRES.W05_TRIP | LV Distribution Boards | LVDB_PRES | W05_TRIP | DI | Outgoing way 5 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10017 | On state = 1 | 3
LV.LVDB_PRES.W05_P | LV Distribution Boards | LVDB_PRES | W05_P | AI | Outgoing way 5 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30040
LV.LVDB_PRES.W06_ON | LV Distribution Boards | LVDB_PRES | W06_ON | DI | Outgoing way 6 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10018
LV.LVDB_PRES.W06_TRIP | LV Distribution Boards | LVDB_PRES | W06_TRIP | DI | Outgoing way 6 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10019 | On state = 1 | 3
LV.LVDB_PRES.W06_P | LV Distribution Boards | LVDB_PRES | W06_P | AI | Outgoing way 6 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30042
LV.LVDB_PRES.W07_ON | LV Distribution Boards | LVDB_PRES | W07_ON | DI | Outgoing way 7 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10020
LV.LVDB_PRES.W07_TRIP | LV Distribution Boards | LVDB_PRES | W07_TRIP | DI | Outgoing way 7 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10021 | On state = 1 | 3
LV.LVDB_PRES.W07_P | LV Distribution Boards | LVDB_PRES | W07_P | AI | Outgoing way 7 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30044
LV.LVDB_PRES.W08_ON | LV Distribution Boards | LVDB_PRES | W08_ON | DI | Outgoing way 8 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10022
LV.LVDB_PRES.W08_TRIP | LV Distribution Boards | LVDB_PRES | W08_TRIP | DI | Outgoing way 8 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10023 | On state = 1 | 3
LV.LVDB_PRES.W08_P | LV Distribution Boards | LVDB_PRES | W08_P | AI | Outgoing way 8 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30046
LV.LVDB_PRES.W09_ON | LV Distribution Boards | LVDB_PRES | W09_ON | DI | Outgoing way 9 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10024
LV.LVDB_PRES.W09_TRIP | LV Distribution Boards | LVDB_PRES | W09_TRIP | DI | Outgoing way 9 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10025 | On state = 1 | 3
LV.LVDB_PRES.W09_P | LV Distribution Boards | LVDB_PRES | W09_P | AI | Outgoing way 9 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30048
LV.LVDB_PRES.W10_ON | LV Distribution Boards | LVDB_PRES | W10_ON | DI | Outgoing way 10 MCCB 250A 36kA ON |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10026
LV.LVDB_PRES.W10_TRIP | LV Distribution Boards | LVDB_PRES | W10_TRIP | DI | Outgoing way 10 tripped |  |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 10027 | On state = 1 | 3
LV.LVDB_PRES.W10_P | LV Distribution Boards | LVDB_PRES | W10_P | AI | Outgoing way 10 active power | kW |  | PM-LVDB_PRES | Modbus RTU / TCP gateway | 30050
LV.LVDB_PM.CB_CLOSED | LV Distribution Boards | LVDB_PM | CB_CLOSED | DI | Incomer ACB 1000A 31.5kA closed |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10001
LV.LVDB_PM.CB_OPEN | LV Distribution Boards | LVDB_PM | CB_OPEN | DI | Incomer ACB 1000A 31.5kA open |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10002
LV.LVDB_PM.CB_TRIPPED | LV Distribution Boards | LVDB_PM | CB_TRIPPED | DI | Incomer ACB 1000A 31.5kA tripped (protection) |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10003 | On state = 1 | 1
LV.LVDB_PM.CB_SPRING | LV Distribution Boards | LVDB_PM | CB_SPRING | DI | Incomer ACB 1000A 31.5kA spring charged |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10004 | On state = 0 | 3
LV.LVDB_PM.CB_RACKED | LV Distribution Boards | LVDB_PM | CB_RACKED | DI | Incomer ACB 1000A 31.5kA racked-in / service position |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10005
LV.LVDB_PM.LR_REMOTE | LV Distribution Boards | LVDB_PM | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10006 | On state = 0 | 4
LV.LVDB_PM.CMD_OPEN | LV Distribution Boards | LVDB_PM | CMD_OPEN | DO | Incomer ACB 1000A 31.5kA open command |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 1
LV.LVDB_PM.CMD_CLOSE | LV Distribution Boards | LVDB_PM | CMD_CLOSE | DO | Incomer ACB 1000A 31.5kA close command |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 2
LV.LVDB_PM.I_L1 | LV Distribution Boards | LVDB_PM | I_L1 | AI | Current L1 | A |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30002
LV.LVDB_PM.I_L2 | LV Distribution Boards | LVDB_PM | I_L2 | AI | Current L2 | A |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30004
LV.LVDB_PM.I_L3 | LV Distribution Boards | LVDB_PM | I_L3 | AI | Current L3 | A |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30006
LV.LVDB_PM.I_N | LV Distribution Boards | LVDB_PM | I_N | AI | Neutral / residual current | A |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30008
LV.LVDB_PM.U_L12 | LV Distribution Boards | LVDB_PM | U_L12 | AI | Voltage L12 | V |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30010
LV.LVDB_PM.U_L23 | LV Distribution Boards | LVDB_PM | U_L23 | AI | Voltage L23 | V |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30012
LV.LVDB_PM.U_L31 | LV Distribution Boards | LVDB_PM | U_L31 | AI | Voltage L31 | V |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30014
LV.LVDB_PM.P | LV Distribution Boards | LVDB_PM | P | AI | Active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30016
LV.LVDB_PM.Q | LV Distribution Boards | LVDB_PM | Q | AI | Reactive power | kvar |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30018
LV.LVDB_PM.S | LV Distribution Boards | LVDB_PM | S | AI | Apparent power | kVA |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30020
LV.LVDB_PM.PF | LV Distribution Boards | LVDB_PM | PF | AI | Power factor |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30022
LV.LVDB_PM.F | LV Distribution Boards | LVDB_PM | F | AI | Frequency | Hz |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30024 | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
LV.LVDB_PM.E_IMP | LV Distribution Boards | LVDB_PM | E_IMP | AI | Active energy import | MWh |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30026
LV.LVDB_PM.E_EXP | LV Distribution Boards | LVDB_PM | E_EXP | AI | Active energy export | MWh |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30028
LV.LVDB_PM.THD_U | LV Distribution Boards | LVDB_PM | THD_U | AI | Voltage THD | % |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30030 | Limits | 1/2 |  |  | 5 | 8
LV.LVDB_PM.SPD_FAIL | LV Distribution Boards | LVDB_PM | SPD_FAIL | DI | LV surge protective device failed |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10007 | On state = 1 | 3
LV.LVDB_PM.W01_ON | LV Distribution Boards | LVDB_PM | W01_ON | DI | Outgoing way 1 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10008
LV.LVDB_PM.W01_TRIP | LV Distribution Boards | LVDB_PM | W01_TRIP | DI | Outgoing way 1 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10009 | On state = 1 | 3
LV.LVDB_PM.W01_P | LV Distribution Boards | LVDB_PM | W01_P | AI | Outgoing way 1 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30032
LV.LVDB_PM.W02_ON | LV Distribution Boards | LVDB_PM | W02_ON | DI | Outgoing way 2 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10010
LV.LVDB_PM.W02_TRIP | LV Distribution Boards | LVDB_PM | W02_TRIP | DI | Outgoing way 2 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10011 | On state = 1 | 3
LV.LVDB_PM.W02_P | LV Distribution Boards | LVDB_PM | W02_P | AI | Outgoing way 2 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30034
LV.LVDB_PM.W03_ON | LV Distribution Boards | LVDB_PM | W03_ON | DI | Outgoing way 3 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10012
LV.LVDB_PM.W03_TRIP | LV Distribution Boards | LVDB_PM | W03_TRIP | DI | Outgoing way 3 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10013 | On state = 1 | 3
LV.LVDB_PM.W03_P | LV Distribution Boards | LVDB_PM | W03_P | AI | Outgoing way 3 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30036
LV.LVDB_PM.W04_ON | LV Distribution Boards | LVDB_PM | W04_ON | DI | Outgoing way 4 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10014
LV.LVDB_PM.W04_TRIP | LV Distribution Boards | LVDB_PM | W04_TRIP | DI | Outgoing way 4 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10015 | On state = 1 | 3
LV.LVDB_PM.W04_P | LV Distribution Boards | LVDB_PM | W04_P | AI | Outgoing way 4 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30038
LV.LVDB_PM.W05_ON | LV Distribution Boards | LVDB_PM | W05_ON | DI | Outgoing way 5 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10016
LV.LVDB_PM.W05_TRIP | LV Distribution Boards | LVDB_PM | W05_TRIP | DI | Outgoing way 5 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10017 | On state = 1 | 3
LV.LVDB_PM.W05_P | LV Distribution Boards | LVDB_PM | W05_P | AI | Outgoing way 5 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30040
LV.LVDB_PM.W06_ON | LV Distribution Boards | LVDB_PM | W06_ON | DI | Outgoing way 6 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10018
LV.LVDB_PM.W06_TRIP | LV Distribution Boards | LVDB_PM | W06_TRIP | DI | Outgoing way 6 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10019 | On state = 1 | 3
LV.LVDB_PM.W06_P | LV Distribution Boards | LVDB_PM | W06_P | AI | Outgoing way 6 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30042
LV.LVDB_PM.W07_ON | LV Distribution Boards | LVDB_PM | W07_ON | DI | Outgoing way 7 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10020
LV.LVDB_PM.W07_TRIP | LV Distribution Boards | LVDB_PM | W07_TRIP | DI | Outgoing way 7 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10021 | On state = 1 | 3
LV.LVDB_PM.W07_P | LV Distribution Boards | LVDB_PM | W07_P | AI | Outgoing way 7 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30044
LV.LVDB_PM.W08_ON | LV Distribution Boards | LVDB_PM | W08_ON | DI | Outgoing way 8 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10022
LV.LVDB_PM.W08_TRIP | LV Distribution Boards | LVDB_PM | W08_TRIP | DI | Outgoing way 8 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10023 | On state = 1 | 3
LV.LVDB_PM.W08_P | LV Distribution Boards | LVDB_PM | W08_P | AI | Outgoing way 8 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30046
LV.LVDB_PM.W09_ON | LV Distribution Boards | LVDB_PM | W09_ON | DI | Outgoing way 9 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10024
LV.LVDB_PM.W09_TRIP | LV Distribution Boards | LVDB_PM | W09_TRIP | DI | Outgoing way 9 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10025 | On state = 1 | 3
LV.LVDB_PM.W09_P | LV Distribution Boards | LVDB_PM | W09_P | AI | Outgoing way 9 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30048
LV.LVDB_PM.W10_ON | LV Distribution Boards | LVDB_PM | W10_ON | DI | Outgoing way 10 MCCB 250A 36kA ON |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10026
LV.LVDB_PM.W10_TRIP | LV Distribution Boards | LVDB_PM | W10_TRIP | DI | Outgoing way 10 tripped |  |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 10027 | On state = 1 | 3
LV.LVDB_PM.W10_P | LV Distribution Boards | LVDB_PM | W10_P | AI | Outgoing way 10 active power | kW |  | PM-LVDB_PM | Modbus RTU / TCP gateway | 30050
LV.AUXPNL.CB_CLOSED | LV Distribution Boards | AUXPNL | CB_CLOSED | DI | Incomer MCCB 200A closed |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10001
LV.AUXPNL.CB_OPEN | LV Distribution Boards | AUXPNL | CB_OPEN | DI | Incomer MCCB 200A open |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10002
LV.AUXPNL.CB_TRIPPED | LV Distribution Boards | AUXPNL | CB_TRIPPED | DI | Incomer MCCB 200A tripped (protection) |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10003 | On state = 1 | 1
LV.AUXPNL.CB_SPRING | LV Distribution Boards | AUXPNL | CB_SPRING | DI | Incomer MCCB 200A spring charged |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10004 | On state = 0 | 3
LV.AUXPNL.LR_REMOTE | LV Distribution Boards | AUXPNL | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10005 | On state = 0 | 4
LV.AUXPNL.CMD_OPEN | LV Distribution Boards | AUXPNL | CMD_OPEN | DO | Incomer MCCB 200A open command |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 1
LV.AUXPNL.CMD_CLOSE | LV Distribution Boards | AUXPNL | CMD_CLOSE | DO | Incomer MCCB 200A close command |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 2
LV.AUXPNL.I_L1 | LV Distribution Boards | AUXPNL | I_L1 | AI | Current L1 | A |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30002
LV.AUXPNL.I_L2 | LV Distribution Boards | AUXPNL | I_L2 | AI | Current L2 | A |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30004
LV.AUXPNL.I_L3 | LV Distribution Boards | AUXPNL | I_L3 | AI | Current L3 | A |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30006
LV.AUXPNL.I_N | LV Distribution Boards | AUXPNL | I_N | AI | Neutral / residual current | A |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30008
LV.AUXPNL.U_L12 | LV Distribution Boards | AUXPNL | U_L12 | AI | Voltage L12 | V |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30010
LV.AUXPNL.U_L23 | LV Distribution Boards | AUXPNL | U_L23 | AI | Voltage L23 | V |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30012
LV.AUXPNL.U_L31 | LV Distribution Boards | AUXPNL | U_L31 | AI | Voltage L31 | V |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30014
LV.AUXPNL.P | LV Distribution Boards | AUXPNL | P | AI | Active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30016
LV.AUXPNL.Q | LV Distribution Boards | AUXPNL | Q | AI | Reactive power | kvar |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30018
LV.AUXPNL.S | LV Distribution Boards | AUXPNL | S | AI | Apparent power | kVA |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30020
LV.AUXPNL.PF | LV Distribution Boards | AUXPNL | PF | AI | Power factor |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30022
LV.AUXPNL.F | LV Distribution Boards | AUXPNL | F | AI | Frequency | Hz |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30024 | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
LV.AUXPNL.E_IMP | LV Distribution Boards | AUXPNL | E_IMP | AI | Active energy import | MWh |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30026
LV.AUXPNL.E_EXP | LV Distribution Boards | AUXPNL | E_EXP | AI | Active energy export | MWh |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30028
LV.AUXPNL.THD_U | LV Distribution Boards | AUXPNL | THD_U | AI | Voltage THD | % |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30030 | Limits | 1/2 |  |  | 5 | 8
LV.AUXPNL.SPD_FAIL | LV Distribution Boards | AUXPNL | SPD_FAIL | DI | LV surge protective device failed |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10006 | On state = 1 | 3
LV.AUXPNL.W01_ON | LV Distribution Boards | AUXPNL | W01_ON | DI | Outgoing way 1 MCB/MCCB ON |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10007
LV.AUXPNL.W01_TRIP | LV Distribution Boards | AUXPNL | W01_TRIP | DI | Outgoing way 1 tripped |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10008 | On state = 1 | 3
LV.AUXPNL.W01_P | LV Distribution Boards | AUXPNL | W01_P | AI | Outgoing way 1 active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30032
LV.AUXPNL.W02_ON | LV Distribution Boards | AUXPNL | W02_ON | DI | Outgoing way 2 MCB/MCCB ON |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10009
LV.AUXPNL.W02_TRIP | LV Distribution Boards | AUXPNL | W02_TRIP | DI | Outgoing way 2 tripped |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10010 | On state = 1 | 3
LV.AUXPNL.W02_P | LV Distribution Boards | AUXPNL | W02_P | AI | Outgoing way 2 active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30034
LV.AUXPNL.W03_ON | LV Distribution Boards | AUXPNL | W03_ON | DI | Outgoing way 3 MCB/MCCB ON |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10011
LV.AUXPNL.W03_TRIP | LV Distribution Boards | AUXPNL | W03_TRIP | DI | Outgoing way 3 tripped |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10012 | On state = 1 | 3
LV.AUXPNL.W03_P | LV Distribution Boards | AUXPNL | W03_P | AI | Outgoing way 3 active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30036
LV.AUXPNL.W04_ON | LV Distribution Boards | AUXPNL | W04_ON | DI | Outgoing way 4 MCB/MCCB ON |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10013
LV.AUXPNL.W04_TRIP | LV Distribution Boards | AUXPNL | W04_TRIP | DI | Outgoing way 4 tripped |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10014 | On state = 1 | 3
LV.AUXPNL.W04_P | LV Distribution Boards | AUXPNL | W04_P | AI | Outgoing way 4 active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30038
LV.AUXPNL.W05_ON | LV Distribution Boards | AUXPNL | W05_ON | DI | Outgoing way 5 MCB/MCCB ON |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10015
LV.AUXPNL.W05_TRIP | LV Distribution Boards | AUXPNL | W05_TRIP | DI | Outgoing way 5 tripped |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10016 | On state = 1 | 3
LV.AUXPNL.W05_P | LV Distribution Boards | AUXPNL | W05_P | AI | Outgoing way 5 active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30040
LV.AUXPNL.W06_ON | LV Distribution Boards | AUXPNL | W06_ON | DI | Outgoing way 6 MCB/MCCB ON |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10017
LV.AUXPNL.W06_TRIP | LV Distribution Boards | AUXPNL | W06_TRIP | DI | Outgoing way 6 tripped |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10018 | On state = 1 | 3
LV.AUXPNL.W06_P | LV Distribution Boards | AUXPNL | W06_P | AI | Outgoing way 6 active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30042
LV.AUXPNL.W07_ON | LV Distribution Boards | AUXPNL | W07_ON | DI | Outgoing way 7 MCB/MCCB ON |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10019
LV.AUXPNL.W07_TRIP | LV Distribution Boards | AUXPNL | W07_TRIP | DI | Outgoing way 7 tripped |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10020 | On state = 1 | 3
LV.AUXPNL.W07_P | LV Distribution Boards | AUXPNL | W07_P | AI | Outgoing way 7 active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30044
LV.AUXPNL.W08_ON | LV Distribution Boards | AUXPNL | W08_ON | DI | Outgoing way 8 MCB/MCCB ON |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10021
LV.AUXPNL.W08_TRIP | LV Distribution Boards | AUXPNL | W08_TRIP | DI | Outgoing way 8 tripped |  |  | PM-AUXPNL | Modbus RTU / TCP gateway | 10022 | On state = 1 | 3
LV.AUXPNL.W08_P | LV Distribution Boards | AUXPNL | W08_P | AI | Outgoing way 8 active power | kW |  | PM-AUXPNL | Modbus RTU / TCP gateway | 30046
DG.DG1.RUNNING | Diesel Generators | DG1 | RUNNING | DI | Generator 1 running |  |  | GCU-DG1 | Modbus TCP | 10001
DG.DG1.READY | Diesel Generators | DG1 | READY | DI | Generator 1 ready / auto mode |  |  | GCU-DG1 | Modbus TCP | 10002 | On state = 0 | 3
DG.DG1.MODE_AUTO | Diesel Generators | DG1 | MODE_AUTO | DI | Generator 1 controller in AUTO |  |  | GCU-DG1 | Modbus TCP | 10003
DG.DG1.SYNC | Diesel Generators | DG1 | SYNC | DI | Generator 1 synchronised |  |  | GCU-DG1 | Modbus TCP | 10004
DG.DG1.COMMON_ALM | Diesel Generators | DG1 | COMMON_ALM | DI | Generator 1 common alarm (warning) |  |  | GCU-DG1 | Modbus TCP | 10005 | On state = 1 | 3
DG.DG1.SHUTDOWN | Diesel Generators | DG1 | SHUTDOWN | DI | Generator 1 shutdown fault |  |  | GCU-DG1 | Modbus TCP | 10006 | On state = 1 | 1
DG.DG1.FAIL_START | Diesel Generators | DG1 | FAIL_START | DI | Generator 1 fail to start |  |  | GCU-DG1 | Modbus TCP | 10007 | On state = 1 | 1
DG.DG1.LOW_OILP | Diesel Generators | DG1 | LOW_OILP | DI | Generator 1 low oil pressure |  |  | GCU-DG1 | Modbus TCP | 10008 | On state = 1 | 1
DG.DG1.HIGH_TEMP | Diesel Generators | DG1 | HIGH_TEMP | DI | Generator 1 high coolant temperature |  |  | GCU-DG1 | Modbus TCP | 10009 | On state = 1 | 1
DG.DG1.OVERSPEED | Diesel Generators | DG1 | OVERSPEED | DI | Generator 1 overspeed |  |  | GCU-DG1 | Modbus TCP | 10010 | On state = 1 | 1
DG.DG1.LOW_FUEL | Diesel Generators | DG1 | LOW_FUEL | DI | Generator 1 low fuel level |  |  | GCU-DG1 | Modbus TCP | 10011 | On state = 1 | 2
DG.DG1.ESTOP | Diesel Generators | DG1 | ESTOP | DI | Generator 1 emergency stop pressed |  |  | GCU-DG1 | Modbus TCP | 10012 | On state = 1 | 1
DG.DG1.BATT_CHG_FAIL | Diesel Generators | DG1 | BATT_CHG_FAIL | DI | Generator 1 battery charger fail |  |  | GCU-DG1 | Modbus TCP | 10013 | On state = 1 | 3
DG.DG1_ACB.CB_CLOSED | Diesel Generators | DG1_ACB | CB_CLOSED | DI | Q1 ACB 800A 65kA closed |  |  | GCU-DG1 | Modbus TCP | 10014
DG.DG1_ACB.CB_OPEN | Diesel Generators | DG1_ACB | CB_OPEN | DI | Q1 ACB 800A 65kA open |  |  | GCU-DG1 | Modbus TCP | 10015
DG.DG1_ACB.CB_TRIPPED | Diesel Generators | DG1_ACB | CB_TRIPPED | DI | Q1 ACB 800A 65kA tripped (protection) |  |  | GCU-DG1 | Modbus TCP | 10016 | On state = 1 | 1
DG.DG1_ACB.CB_SPRING | Diesel Generators | DG1_ACB | CB_SPRING | DI | Q1 ACB 800A 65kA spring charged |  |  | GCU-DG1 | Modbus TCP | 10017 | On state = 0 | 3
DG.DG1_ACB.CB_RACKED | Diesel Generators | DG1_ACB | CB_RACKED | DI | Q1 ACB 800A 65kA racked-in / service position |  |  | GCU-DG1 | Modbus TCP | 10018
DG.DG1_ACB.LR_REMOTE | Diesel Generators | DG1_ACB | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | GCU-DG1 | Modbus TCP | 10019 | On state = 0 | 4
DG.DG1_ACB.CMD_OPEN | Diesel Generators | DG1_ACB | CMD_OPEN | DO | Q1 ACB 800A 65kA open command |  |  | GCU-DG1 | Modbus TCP | 1
DG.DG1_ACB.CMD_CLOSE | Diesel Generators | DG1_ACB | CMD_CLOSE | DO | Q1 ACB 800A 65kA close command |  |  | GCU-DG1 | Modbus TCP | 2
DG.DG1.I_L1 | Diesel Generators | DG1 | I_L1 | AI | Current L1 | A |  | GCU-DG1 | Modbus TCP | 30002
DG.DG1.I_L2 | Diesel Generators | DG1 | I_L2 | AI | Current L2 | A |  | GCU-DG1 | Modbus TCP | 30004
DG.DG1.I_L3 | Diesel Generators | DG1 | I_L3 | AI | Current L3 | A |  | GCU-DG1 | Modbus TCP | 30006
DG.DG1.U_L12 | Diesel Generators | DG1 | U_L12 | AI | Voltage L12 | V |  | GCU-DG1 | Modbus TCP | 30008
DG.DG1.U_L23 | Diesel Generators | DG1 | U_L23 | AI | Voltage L23 | V |  | GCU-DG1 | Modbus TCP | 30010
DG.DG1.U_L31 | Diesel Generators | DG1 | U_L31 | AI | Voltage L31 | V |  | GCU-DG1 | Modbus TCP | 30012
DG.DG1.P | Diesel Generators | DG1 | P | AI | Active power | kW |  | GCU-DG1 | Modbus TCP | 30014
DG.DG1.Q | Diesel Generators | DG1 | Q | AI | Reactive power | kvar |  | GCU-DG1 | Modbus TCP | 30016
DG.DG1.S | Diesel Generators | DG1 | S | AI | Apparent power | kVA |  | GCU-DG1 | Modbus TCP | 30018
DG.DG1.PF | Diesel Generators | DG1 | PF | AI | Power factor |  |  | GCU-DG1 | Modbus TCP | 30020
DG.DG1.F | Diesel Generators | DG1 | F | AI | Frequency | Hz |  | GCU-DG1 | Modbus TCP | 30022 | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
DG.DG1.E_IMP | Diesel Generators | DG1 | E_IMP | AI | Active energy import | MWh |  | GCU-DG1 | Modbus TCP | 30024
DG.DG1.E_EXP | Diesel Generators | DG1 | E_EXP | AI | Active energy export | MWh |  | GCU-DG1 | Modbus TCP | 30026
DG.DG1.LOAD_PCT | Diesel Generators | DG1 | LOAD_PCT | AI | Generator 1 load | % |  | GCU-DG1 | Modbus TCP | 30028
DG.DG1.RPM | Diesel Generators | DG1 | RPM | AI | Engine speed | rpm |  | GCU-DG1 | Modbus TCP | 30030
DG.DG1.OIL_P | Diesel Generators | DG1 | OIL_P | AI | Oil pressure | bar |  | GCU-DG1 | Modbus TCP | 30032
DG.DG1.COOL_T | Diesel Generators | DG1 | COOL_T | AI | Coolant temperature | °C |  | GCU-DG1 | Modbus TCP | 30034 | Limits | 1/2 |  |  | 95 | 103
DG.DG1.FUEL | Diesel Generators | DG1 | FUEL | AI | Fuel level | % |  | GCU-DG1 | Modbus TCP | 30036 | Limits | 1/2 | 10 | 25
DG.DG1.FUEL_RATE | Diesel Generators | DG1 | FUEL_RATE | AI | Fuel consumption | L/h |  | GCU-DG1 | Modbus TCP | 30038
DG.DG1.BATT_V | Diesel Generators | DG1 | BATT_V | AI | Starter battery voltage | V |  | GCU-DG1 | Modbus TCP | 30040 | Limits | 1/2 |  | 23 | 29
DG.DG1.HOURS | Diesel Generators | DG1 | HOURS | AI | Running hours | h |  | GCU-DG1 | Modbus TCP | 30042
DG.DG1.STARTS | Diesel Generators | DG1 | STARTS | AI | Number of starts |  |  | GCU-DG1 | Modbus TCP | 30044
DG.DG1.CMD_START | Diesel Generators | DG1 | CMD_START | DO | Generator 1 remote start |  |  | GCU-DG1 | Modbus TCP | 3
DG.DG1.CMD_STOP | Diesel Generators | DG1 | CMD_STOP | DO | Generator 1 remote stop |  |  | GCU-DG1 | Modbus TCP | 4
DG.DG1.CMD_RESET | Diesel Generators | DG1 | CMD_RESET | DO | Generator 1 fault reset |  |  | GCU-DG1 | Modbus TCP | 5
DG.DG1.SP_P | Diesel Generators | DG1 | SP_P | AO | Generator 1 active power setpoint | kW | 0-440 | GCU-DG1 | Modbus TCP | 40002
DG.DG2.RUNNING | Diesel Generators | DG2 | RUNNING | DI | Generator 2 running |  |  | GCU-DG2 | Modbus TCP | 10001
DG.DG2.READY | Diesel Generators | DG2 | READY | DI | Generator 2 ready / auto mode |  |  | GCU-DG2 | Modbus TCP | 10002 | On state = 0 | 3
DG.DG2.MODE_AUTO | Diesel Generators | DG2 | MODE_AUTO | DI | Generator 2 controller in AUTO |  |  | GCU-DG2 | Modbus TCP | 10003
DG.DG2.SYNC | Diesel Generators | DG2 | SYNC | DI | Generator 2 synchronised |  |  | GCU-DG2 | Modbus TCP | 10004
DG.DG2.COMMON_ALM | Diesel Generators | DG2 | COMMON_ALM | DI | Generator 2 common alarm (warning) |  |  | GCU-DG2 | Modbus TCP | 10005 | On state = 1 | 3
DG.DG2.SHUTDOWN | Diesel Generators | DG2 | SHUTDOWN | DI | Generator 2 shutdown fault |  |  | GCU-DG2 | Modbus TCP | 10006 | On state = 1 | 1
DG.DG2.FAIL_START | Diesel Generators | DG2 | FAIL_START | DI | Generator 2 fail to start |  |  | GCU-DG2 | Modbus TCP | 10007 | On state = 1 | 1
DG.DG2.LOW_OILP | Diesel Generators | DG2 | LOW_OILP | DI | Generator 2 low oil pressure |  |  | GCU-DG2 | Modbus TCP | 10008 | On state = 1 | 1
DG.DG2.HIGH_TEMP | Diesel Generators | DG2 | HIGH_TEMP | DI | Generator 2 high coolant temperature |  |  | GCU-DG2 | Modbus TCP | 10009 | On state = 1 | 1
DG.DG2.OVERSPEED | Diesel Generators | DG2 | OVERSPEED | DI | Generator 2 overspeed |  |  | GCU-DG2 | Modbus TCP | 10010 | On state = 1 | 1
DG.DG2.LOW_FUEL | Diesel Generators | DG2 | LOW_FUEL | DI | Generator 2 low fuel level |  |  | GCU-DG2 | Modbus TCP | 10011 | On state = 1 | 2
DG.DG2.ESTOP | Diesel Generators | DG2 | ESTOP | DI | Generator 2 emergency stop pressed |  |  | GCU-DG2 | Modbus TCP | 10012 | On state = 1 | 1
DG.DG2.BATT_CHG_FAIL | Diesel Generators | DG2 | BATT_CHG_FAIL | DI | Generator 2 battery charger fail |  |  | GCU-DG2 | Modbus TCP | 10013 | On state = 1 | 3
DG.DG2_ACB.CB_CLOSED | Diesel Generators | DG2_ACB | CB_CLOSED | DI | Q2 ACB 1000A 65kA closed |  |  | GCU-DG2 | Modbus TCP | 10014
DG.DG2_ACB.CB_OPEN | Diesel Generators | DG2_ACB | CB_OPEN | DI | Q2 ACB 1000A 65kA open |  |  | GCU-DG2 | Modbus TCP | 10015
DG.DG2_ACB.CB_TRIPPED | Diesel Generators | DG2_ACB | CB_TRIPPED | DI | Q2 ACB 1000A 65kA tripped (protection) |  |  | GCU-DG2 | Modbus TCP | 10016 | On state = 1 | 1
DG.DG2_ACB.CB_SPRING | Diesel Generators | DG2_ACB | CB_SPRING | DI | Q2 ACB 1000A 65kA spring charged |  |  | GCU-DG2 | Modbus TCP | 10017 | On state = 0 | 3
DG.DG2_ACB.CB_RACKED | Diesel Generators | DG2_ACB | CB_RACKED | DI | Q2 ACB 1000A 65kA racked-in / service position |  |  | GCU-DG2 | Modbus TCP | 10018
DG.DG2_ACB.LR_REMOTE | Diesel Generators | DG2_ACB | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | GCU-DG2 | Modbus TCP | 10019 | On state = 0 | 4
DG.DG2_ACB.CMD_OPEN | Diesel Generators | DG2_ACB | CMD_OPEN | DO | Q2 ACB 1000A 65kA open command |  |  | GCU-DG2 | Modbus TCP | 1
DG.DG2_ACB.CMD_CLOSE | Diesel Generators | DG2_ACB | CMD_CLOSE | DO | Q2 ACB 1000A 65kA close command |  |  | GCU-DG2 | Modbus TCP | 2
DG.DG2.I_L1 | Diesel Generators | DG2 | I_L1 | AI | Current L1 | A |  | GCU-DG2 | Modbus TCP | 30002
DG.DG2.I_L2 | Diesel Generators | DG2 | I_L2 | AI | Current L2 | A |  | GCU-DG2 | Modbus TCP | 30004
DG.DG2.I_L3 | Diesel Generators | DG2 | I_L3 | AI | Current L3 | A |  | GCU-DG2 | Modbus TCP | 30006
DG.DG2.U_L12 | Diesel Generators | DG2 | U_L12 | AI | Voltage L12 | V |  | GCU-DG2 | Modbus TCP | 30008
DG.DG2.U_L23 | Diesel Generators | DG2 | U_L23 | AI | Voltage L23 | V |  | GCU-DG2 | Modbus TCP | 30010
DG.DG2.U_L31 | Diesel Generators | DG2 | U_L31 | AI | Voltage L31 | V |  | GCU-DG2 | Modbus TCP | 30012
DG.DG2.P | Diesel Generators | DG2 | P | AI | Active power | kW |  | GCU-DG2 | Modbus TCP | 30014
DG.DG2.Q | Diesel Generators | DG2 | Q | AI | Reactive power | kvar |  | GCU-DG2 | Modbus TCP | 30016
DG.DG2.S | Diesel Generators | DG2 | S | AI | Apparent power | kVA |  | GCU-DG2 | Modbus TCP | 30018
DG.DG2.PF | Diesel Generators | DG2 | PF | AI | Power factor |  |  | GCU-DG2 | Modbus TCP | 30020
DG.DG2.F | Diesel Generators | DG2 | F | AI | Frequency | Hz |  | GCU-DG2 | Modbus TCP | 30022 | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
DG.DG2.E_IMP | Diesel Generators | DG2 | E_IMP | AI | Active energy import | MWh |  | GCU-DG2 | Modbus TCP | 30024
DG.DG2.E_EXP | Diesel Generators | DG2 | E_EXP | AI | Active energy export | MWh |  | GCU-DG2 | Modbus TCP | 30026
DG.DG2.LOAD_PCT | Diesel Generators | DG2 | LOAD_PCT | AI | Generator 2 load | % |  | GCU-DG2 | Modbus TCP | 30028
DG.DG2.RPM | Diesel Generators | DG2 | RPM | AI | Engine speed | rpm |  | GCU-DG2 | Modbus TCP | 30030
DG.DG2.OIL_P | Diesel Generators | DG2 | OIL_P | AI | Oil pressure | bar |  | GCU-DG2 | Modbus TCP | 30032
DG.DG2.COOL_T | Diesel Generators | DG2 | COOL_T | AI | Coolant temperature | °C |  | GCU-DG2 | Modbus TCP | 30034 | Limits | 1/2 |  |  | 95 | 103
DG.DG2.FUEL | Diesel Generators | DG2 | FUEL | AI | Fuel level | % |  | GCU-DG2 | Modbus TCP | 30036 | Limits | 1/2 | 10 | 25
DG.DG2.FUEL_RATE | Diesel Generators | DG2 | FUEL_RATE | AI | Fuel consumption | L/h |  | GCU-DG2 | Modbus TCP | 30038
DG.DG2.BATT_V | Diesel Generators | DG2 | BATT_V | AI | Starter battery voltage | V |  | GCU-DG2 | Modbus TCP | 30040 | Limits | 1/2 |  | 23 | 29
DG.DG2.HOURS | Diesel Generators | DG2 | HOURS | AI | Running hours | h |  | GCU-DG2 | Modbus TCP | 30042
DG.DG2.STARTS | Diesel Generators | DG2 | STARTS | AI | Number of starts |  |  | GCU-DG2 | Modbus TCP | 30044
DG.DG2.CMD_START | Diesel Generators | DG2 | CMD_START | DO | Generator 2 remote start |  |  | GCU-DG2 | Modbus TCP | 3
DG.DG2.CMD_STOP | Diesel Generators | DG2 | CMD_STOP | DO | Generator 2 remote stop |  |  | GCU-DG2 | Modbus TCP | 4
DG.DG2.CMD_RESET | Diesel Generators | DG2 | CMD_RESET | DO | Generator 2 fault reset |  |  | GCU-DG2 | Modbus TCP | 5
DG.DG2.SP_P | Diesel Generators | DG2 | SP_P | AO | Generator 2 active power setpoint | kW | 0-528 | GCU-DG2 | Modbus TCP | 40002
DG.TX_LV.CB_CLOSED | Diesel Generators | TX_LV | CB_CLOSED | DI | DG step-up TX LV ACB closed |  |  | PM-DGTX | Modbus RTU | 10001
DG.TX_LV.CB_OPEN | Diesel Generators | TX_LV | CB_OPEN | DI | DG step-up TX LV ACB open |  |  | PM-DGTX | Modbus RTU | 10002
DG.TX_LV.CB_TRIPPED | Diesel Generators | TX_LV | CB_TRIPPED | DI | DG step-up TX LV ACB tripped (protection) |  |  | PM-DGTX | Modbus RTU | 10003 | On state = 1 | 1
DG.TX_LV.CB_SPRING | Diesel Generators | TX_LV | CB_SPRING | DI | DG step-up TX LV ACB spring charged |  |  | PM-DGTX | Modbus RTU | 10004 | On state = 0 | 3
DG.TX_LV.CB_RACKED | Diesel Generators | TX_LV | CB_RACKED | DI | DG step-up TX LV ACB racked-in / service position |  |  | PM-DGTX | Modbus RTU | 10005
DG.TX_LV.LR_REMOTE | Diesel Generators | TX_LV | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | PM-DGTX | Modbus RTU | 10006 | On state = 0 | 4
DG.TX_LV.CMD_OPEN | Diesel Generators | TX_LV | CMD_OPEN | DO | DG step-up TX LV ACB open command |  |  | PM-DGTX | Modbus RTU | 1
DG.TX_LV.CMD_CLOSE | Diesel Generators | TX_LV | CMD_CLOSE | DO | DG step-up TX LV ACB close command |  |  | PM-DGTX | Modbus RTU | 2
PV.LV_ACB.CB_CLOSED | PV Plant / Inverters | LV_ACB | CB_CLOSED | DI | PV LV ACB 1250A closed |  |  | PM-PVTX | Modbus RTU | 10001
PV.LV_ACB.CB_OPEN | PV Plant / Inverters | LV_ACB | CB_OPEN | DI | PV LV ACB 1250A open |  |  | PM-PVTX | Modbus RTU | 10002
PV.LV_ACB.CB_TRIPPED | PV Plant / Inverters | LV_ACB | CB_TRIPPED | DI | PV LV ACB 1250A tripped (protection) |  |  | PM-PVTX | Modbus RTU | 10003 | On state = 1 | 1
PV.LV_ACB.CB_SPRING | PV Plant / Inverters | LV_ACB | CB_SPRING | DI | PV LV ACB 1250A spring charged |  |  | PM-PVTX | Modbus RTU | 10004 | On state = 0 | 3
PV.LV_ACB.CB_RACKED | PV Plant / Inverters | LV_ACB | CB_RACKED | DI | PV LV ACB 1250A racked-in / service position |  |  | PM-PVTX | Modbus RTU | 10005
PV.LV_ACB.LR_REMOTE | PV Plant / Inverters | LV_ACB | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | PM-PVTX | Modbus RTU | 10006 | On state = 0 | 4
PV.LV_ACB.CMD_OPEN | PV Plant / Inverters | LV_ACB | CMD_OPEN | DO | PV LV ACB 1250A open command |  |  | PM-PVTX | Modbus RTU | 1
PV.LV_ACB.CMD_CLOSE | PV Plant / Inverters | LV_ACB | CMD_CLOSE | DO | PV LV ACB 1250A close command |  |  | PM-PVTX | Modbus RTU | 2
PV.POC.I_L1 | PV Plant / Inverters | POC | I_L1 | AI | Current L1 | A |  | PM-PVTX | Modbus RTU | 30002
PV.POC.I_L2 | PV Plant / Inverters | POC | I_L2 | AI | Current L2 | A |  | PM-PVTX | Modbus RTU | 30004
PV.POC.I_L3 | PV Plant / Inverters | POC | I_L3 | AI | Current L3 | A |  | PM-PVTX | Modbus RTU | 30006
PV.POC.U_L12 | PV Plant / Inverters | POC | U_L12 | AI | Voltage L12 | V |  | PM-PVTX | Modbus RTU | 30008
PV.POC.U_L23 | PV Plant / Inverters | POC | U_L23 | AI | Voltage L23 | V |  | PM-PVTX | Modbus RTU | 30010
PV.POC.U_L31 | PV Plant / Inverters | POC | U_L31 | AI | Voltage L31 | V |  | PM-PVTX | Modbus RTU | 30012
PV.POC.P | PV Plant / Inverters | POC | P | AI | Active power | kW |  | PM-PVTX | Modbus RTU | 30014
PV.POC.Q | PV Plant / Inverters | POC | Q | AI | Reactive power | kvar |  | PM-PVTX | Modbus RTU | 30016
PV.POC.S | PV Plant / Inverters | POC | S | AI | Apparent power | kVA |  | PM-PVTX | Modbus RTU | 30018
PV.POC.PF | PV Plant / Inverters | POC | PF | AI | Power factor |  |  | PM-PVTX | Modbus RTU | 30020
PV.POC.F | PV Plant / Inverters | POC | F | AI | Frequency | Hz |  | PM-PVTX | Modbus RTU | 30022 | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
PV.POC.E_IMP | PV Plant / Inverters | POC | E_IMP | AI | Active energy import | MWh |  | PM-PVTX | Modbus RTU | 30024
PV.POC.E_EXP | PV Plant / Inverters | POC | E_EXP | AI | Active energy export | MWh |  | PM-PVTX | Modbus RTU | 30026
PV.POC.THD_U | PV Plant / Inverters | POC | THD_U | AI | Voltage THD | % |  | PM-PVTX | Modbus RTU | 30028 | Limits | 1/2 |  |  | 5 | 8
PV.INV1.RUN | PV Plant / Inverters | INV1 | RUN | DI | NB01 running (grid-connected) |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10001
PV.INV1.STANDBY | PV Plant / Inverters | INV1 | STANDBY | DI | NB01 standby / derating |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10002
PV.INV1.FAULT | PV Plant / Inverters | INV1 | FAULT | DI | NB01 fault |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10003 | On state = 1 | 2
PV.INV1.COMM | PV Plant / Inverters | INV1 | COMM | DI | NB01 communication OK |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10004 | On state = 0 | 2
PV.INV1.ISO_FLT | PV Plant / Inverters | INV1 | ISO_FLT | DI | NB01 insulation (PV-earth) fault |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10005 | On state = 1 | 2
PV.INV1.DC_SPD | PV Plant / Inverters | INV1 | DC_SPD | DI | NB01 DC SPD failed |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10006 | On state = 1 | 3
PV.INV1.AC_SPD | PV Plant / Inverters | INV1 | AC_SPD | DI | NB01 AC SPD failed |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10007 | On state = 1 | 3
PV.INV1.MCCB_ON | PV Plant / Inverters | INV1 | MCCB_ON | DI | NB01 AC MCCB 400A 36kA ON |  |  | PM-PVTX | Modbus RTU | 10007 | On state = 0 | 2
PV.INV1.P | PV Plant / Inverters | INV1 | P | AI | NB01 AC active power | kW |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30002
PV.INV1.Q | PV Plant / Inverters | INV1 | Q | AI | NB01 AC reactive power | kvar |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30004
PV.INV1.PF | PV Plant / Inverters | INV1 | PF | AI | NB01 power factor |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30006
PV.INV1.U_AC | PV Plant / Inverters | INV1 | U_AC | AI | NB01 AC voltage L-L | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30008
PV.INV1.I_AC | PV Plant / Inverters | INV1 | I_AC | AI | NB01 AC current | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30010
PV.INV1.F | PV Plant / Inverters | INV1 | F | AI | NB01 grid frequency | Hz |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30012
PV.INV1.P_DC | PV Plant / Inverters | INV1 | P_DC | AI | NB01 DC power | kW |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30014
PV.INV1.U_DC | PV Plant / Inverters | INV1 | U_DC | AI | NB01 DC bus voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30016
PV.INV1.T_INT | PV Plant / Inverters | INV1 | T_INT | AI | NB01 internal temperature | °C |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30018 | Limits | 1/2 |  |  | 70 | 80
PV.INV1.EFF | PV Plant / Inverters | INV1 | EFF | AI | NB01 conversion efficiency | % |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30020
PV.INV1.R_ISO | PV Plant / Inverters | INV1 | R_ISO | AI | NB01 insulation resistance | kΩ |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30022 | Limits | 1/2 |  | 200
PV.INV1.E_DAY | PV Plant / Inverters | INV1 | E_DAY | AI | NB01 energy today | kWh |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30024
PV.INV1.E_TOT | PV Plant / Inverters | INV1 | E_TOT | AI | NB01 energy total | MWh |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30026
PV.INV1.MPPT01_U | PV Plant / Inverters | INV1 | MPPT01_U | AI | NB01 MPPT1 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30028
PV.INV1.MPPT02_U | PV Plant / Inverters | INV1 | MPPT02_U | AI | NB01 MPPT2 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30030
PV.INV1.MPPT03_U | PV Plant / Inverters | INV1 | MPPT03_U | AI | NB01 MPPT3 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30032
PV.INV1.MPPT04_U | PV Plant / Inverters | INV1 | MPPT04_U | AI | NB01 MPPT4 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30034
PV.INV1.MPPT05_U | PV Plant / Inverters | INV1 | MPPT05_U | AI | NB01 MPPT5 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30036
PV.INV1.MPPT06_U | PV Plant / Inverters | INV1 | MPPT06_U | AI | NB01 MPPT6 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30038
PV.INV1.MPPT07_U | PV Plant / Inverters | INV1 | MPPT07_U | AI | NB01 MPPT7 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30040
PV.INV1.MPPT08_U | PV Plant / Inverters | INV1 | MPPT08_U | AI | NB01 MPPT8 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30042
PV.INV1.MPPT09_U | PV Plant / Inverters | INV1 | MPPT09_U | AI | NB01 MPPT9 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30044
PV.INV1.MPPT10_U | PV Plant / Inverters | INV1 | MPPT10_U | AI | NB01 MPPT10 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30046
PV.INV1.MPPT11_U | PV Plant / Inverters | INV1 | MPPT11_U | AI | NB01 MPPT11 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30048
PV.INV1.MPPT12_U | PV Plant / Inverters | INV1 | MPPT12_U | AI | NB01 MPPT12 voltage | V |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30050
PV.INV1.STR01_I | PV Plant / Inverters | INV1 | STR01_I | AI | NB01-01 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30052
PV.INV1.STR02_I | PV Plant / Inverters | INV1 | STR02_I | AI | NB01-02 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30054
PV.INV1.STR03_I | PV Plant / Inverters | INV1 | STR03_I | AI | NB01-03 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30056
PV.INV1.STR04_I | PV Plant / Inverters | INV1 | STR04_I | AI | NB01-04 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30058
PV.INV1.STR05_I | PV Plant / Inverters | INV1 | STR05_I | AI | NB01-05 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30060
PV.INV1.STR06_I | PV Plant / Inverters | INV1 | STR06_I | AI | NB01-06 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30062
PV.INV1.STR07_I | PV Plant / Inverters | INV1 | STR07_I | AI | NB01-07 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30064
PV.INV1.STR08_I | PV Plant / Inverters | INV1 | STR08_I | AI | NB01-08 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30066
PV.INV1.STR09_I | PV Plant / Inverters | INV1 | STR09_I | AI | NB01-09 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30068
PV.INV1.STR10_I | PV Plant / Inverters | INV1 | STR10_I | AI | NB01-10 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30070
PV.INV1.STR11_I | PV Plant / Inverters | INV1 | STR11_I | AI | NB01-11 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30072
PV.INV1.STR12_I | PV Plant / Inverters | INV1 | STR12_I | AI | NB01-12 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30074
PV.INV1.STR13_I | PV Plant / Inverters | INV1 | STR13_I | AI | NB01-13 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30076
PV.INV1.STR14_I | PV Plant / Inverters | INV1 | STR14_I | AI | NB01-14 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30078
PV.INV1.STR15_I | PV Plant / Inverters | INV1 | STR15_I | AI | NB01-15 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30080
PV.INV1.STR16_I | PV Plant / Inverters | INV1 | STR16_I | AI | NB01-16 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30082
PV.INV1.STR17_I | PV Plant / Inverters | INV1 | STR17_I | AI | NB01-17 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30084
PV.INV1.STR18_I | PV Plant / Inverters | INV1 | STR18_I | AI | NB01-18 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30086
PV.INV1.STR19_I | PV Plant / Inverters | INV1 | STR19_I | AI | NB01-19 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30088
PV.INV1.STR20_I | PV Plant / Inverters | INV1 | STR20_I | AI | NB01-20 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30090
PV.INV1.STR21_I | PV Plant / Inverters | INV1 | STR21_I | AI | NB01-21 string current (26 modules) | A |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30092
PV.INV1.CMD_START | PV Plant / Inverters | INV1 | CMD_START | DO | NB01 start / power on |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 1
PV.INV1.CMD_STOP | PV Plant / Inverters | INV1 | CMD_STOP | DO | NB01 stop / power off |  |  | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 2
PV.INV1.SP_PLIM | PV Plant / Inverters | INV1 | SP_PLIM | AO | NB01 active power limit | % | 0-100 | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 40002
PV.INV1.SP_PF | PV Plant / Inverters | INV1 | SP_PF | AO | NB01 power factor setpoint |  | 0.8i-0.8c | NB01 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 40004
PV.INV2.RUN | PV Plant / Inverters | INV2 | RUN | DI | NB02 running (grid-connected) |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10001
PV.INV2.STANDBY | PV Plant / Inverters | INV2 | STANDBY | DI | NB02 standby / derating |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10002
PV.INV2.FAULT | PV Plant / Inverters | INV2 | FAULT | DI | NB02 fault |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10003 | On state = 1 | 2
PV.INV2.COMM | PV Plant / Inverters | INV2 | COMM | DI | NB02 communication OK |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10004 | On state = 0 | 2
PV.INV2.ISO_FLT | PV Plant / Inverters | INV2 | ISO_FLT | DI | NB02 insulation (PV-earth) fault |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10005 | On state = 1 | 2
PV.INV2.DC_SPD | PV Plant / Inverters | INV2 | DC_SPD | DI | NB02 DC SPD failed |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10006 | On state = 1 | 3
PV.INV2.AC_SPD | PV Plant / Inverters | INV2 | AC_SPD | DI | NB02 AC SPD failed |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10007 | On state = 1 | 3
PV.INV2.MCCB_ON | PV Plant / Inverters | INV2 | MCCB_ON | DI | NB02 AC MCCB 400A 36kA ON |  |  | PM-PVTX | Modbus RTU | 10008 | On state = 0 | 2
PV.INV2.P | PV Plant / Inverters | INV2 | P | AI | NB02 AC active power | kW |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30002
PV.INV2.Q | PV Plant / Inverters | INV2 | Q | AI | NB02 AC reactive power | kvar |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30004
PV.INV2.PF | PV Plant / Inverters | INV2 | PF | AI | NB02 power factor |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30006
PV.INV2.U_AC | PV Plant / Inverters | INV2 | U_AC | AI | NB02 AC voltage L-L | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30008
PV.INV2.I_AC | PV Plant / Inverters | INV2 | I_AC | AI | NB02 AC current | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30010
PV.INV2.F | PV Plant / Inverters | INV2 | F | AI | NB02 grid frequency | Hz |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30012
PV.INV2.P_DC | PV Plant / Inverters | INV2 | P_DC | AI | NB02 DC power | kW |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30014
PV.INV2.U_DC | PV Plant / Inverters | INV2 | U_DC | AI | NB02 DC bus voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30016
PV.INV2.T_INT | PV Plant / Inverters | INV2 | T_INT | AI | NB02 internal temperature | °C |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30018 | Limits | 1/2 |  |  | 70 | 80
PV.INV2.EFF | PV Plant / Inverters | INV2 | EFF | AI | NB02 conversion efficiency | % |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30020
PV.INV2.R_ISO | PV Plant / Inverters | INV2 | R_ISO | AI | NB02 insulation resistance | kΩ |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30022 | Limits | 1/2 |  | 200
PV.INV2.E_DAY | PV Plant / Inverters | INV2 | E_DAY | AI | NB02 energy today | kWh |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30024
PV.INV2.E_TOT | PV Plant / Inverters | INV2 | E_TOT | AI | NB02 energy total | MWh |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30026
PV.INV2.MPPT01_U | PV Plant / Inverters | INV2 | MPPT01_U | AI | NB02 MPPT1 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30028
PV.INV2.MPPT02_U | PV Plant / Inverters | INV2 | MPPT02_U | AI | NB02 MPPT2 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30030
PV.INV2.MPPT03_U | PV Plant / Inverters | INV2 | MPPT03_U | AI | NB02 MPPT3 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30032
PV.INV2.MPPT04_U | PV Plant / Inverters | INV2 | MPPT04_U | AI | NB02 MPPT4 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30034
PV.INV2.MPPT05_U | PV Plant / Inverters | INV2 | MPPT05_U | AI | NB02 MPPT5 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30036
PV.INV2.MPPT06_U | PV Plant / Inverters | INV2 | MPPT06_U | AI | NB02 MPPT6 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30038
PV.INV2.MPPT07_U | PV Plant / Inverters | INV2 | MPPT07_U | AI | NB02 MPPT7 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30040
PV.INV2.MPPT08_U | PV Plant / Inverters | INV2 | MPPT08_U | AI | NB02 MPPT8 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30042
PV.INV2.MPPT09_U | PV Plant / Inverters | INV2 | MPPT09_U | AI | NB02 MPPT9 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30044
PV.INV2.MPPT10_U | PV Plant / Inverters | INV2 | MPPT10_U | AI | NB02 MPPT10 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30046
PV.INV2.MPPT11_U | PV Plant / Inverters | INV2 | MPPT11_U | AI | NB02 MPPT11 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30048
PV.INV2.MPPT12_U | PV Plant / Inverters | INV2 | MPPT12_U | AI | NB02 MPPT12 voltage | V |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30050
PV.INV2.STR01_I | PV Plant / Inverters | INV2 | STR01_I | AI | NB02-01 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30052
PV.INV2.STR02_I | PV Plant / Inverters | INV2 | STR02_I | AI | NB02-02 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30054
PV.INV2.STR03_I | PV Plant / Inverters | INV2 | STR03_I | AI | NB02-03 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30056
PV.INV2.STR04_I | PV Plant / Inverters | INV2 | STR04_I | AI | NB02-04 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30058
PV.INV2.STR05_I | PV Plant / Inverters | INV2 | STR05_I | AI | NB02-05 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30060
PV.INV2.STR06_I | PV Plant / Inverters | INV2 | STR06_I | AI | NB02-06 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30062
PV.INV2.STR07_I | PV Plant / Inverters | INV2 | STR07_I | AI | NB02-07 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30064
PV.INV2.STR08_I | PV Plant / Inverters | INV2 | STR08_I | AI | NB02-08 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30066
PV.INV2.STR09_I | PV Plant / Inverters | INV2 | STR09_I | AI | NB02-09 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30068
PV.INV2.STR10_I | PV Plant / Inverters | INV2 | STR10_I | AI | NB02-10 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30070
PV.INV2.STR11_I | PV Plant / Inverters | INV2 | STR11_I | AI | NB02-11 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30072
PV.INV2.STR12_I | PV Plant / Inverters | INV2 | STR12_I | AI | NB02-12 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30074
PV.INV2.STR13_I | PV Plant / Inverters | INV2 | STR13_I | AI | NB02-13 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30076
PV.INV2.STR14_I | PV Plant / Inverters | INV2 | STR14_I | AI | NB02-14 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30078
PV.INV2.STR15_I | PV Plant / Inverters | INV2 | STR15_I | AI | NB02-15 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30080
PV.INV2.STR16_I | PV Plant / Inverters | INV2 | STR16_I | AI | NB02-16 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30082
PV.INV2.STR17_I | PV Plant / Inverters | INV2 | STR17_I | AI | NB02-17 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30084
PV.INV2.STR18_I | PV Plant / Inverters | INV2 | STR18_I | AI | NB02-18 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30086
PV.INV2.STR19_I | PV Plant / Inverters | INV2 | STR19_I | AI | NB02-19 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30088
PV.INV2.STR20_I | PV Plant / Inverters | INV2 | STR20_I | AI | NB02-20 string current (26 modules) | A |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30090
PV.INV2.CMD_START | PV Plant / Inverters | INV2 | CMD_START | DO | NB02 start / power on |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 1
PV.INV2.CMD_STOP | PV Plant / Inverters | INV2 | CMD_STOP | DO | NB02 stop / power off |  |  | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 2
PV.INV2.SP_PLIM | PV Plant / Inverters | INV2 | SP_PLIM | AO | NB02 active power limit | % | 0-100 | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 40002
PV.INV2.SP_PF | PV Plant / Inverters | INV2 | SP_PF | AO | NB02 power factor setpoint |  | 0.8i-0.8c | NB02 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 40004
PV.INV3.RUN | PV Plant / Inverters | INV3 | RUN | DI | NB03 running (grid-connected) |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10001
PV.INV3.STANDBY | PV Plant / Inverters | INV3 | STANDBY | DI | NB03 standby / derating |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10002
PV.INV3.FAULT | PV Plant / Inverters | INV3 | FAULT | DI | NB03 fault |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10003 | On state = 1 | 2
PV.INV3.COMM | PV Plant / Inverters | INV3 | COMM | DI | NB03 communication OK |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10004 | On state = 0 | 2
PV.INV3.ISO_FLT | PV Plant / Inverters | INV3 | ISO_FLT | DI | NB03 insulation (PV-earth) fault |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10005 | On state = 1 | 2
PV.INV3.DC_SPD | PV Plant / Inverters | INV3 | DC_SPD | DI | NB03 DC SPD failed |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10006 | On state = 1 | 3
PV.INV3.AC_SPD | PV Plant / Inverters | INV3 | AC_SPD | DI | NB03 AC SPD failed |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10007 | On state = 1 | 3
PV.INV3.MCCB_ON | PV Plant / Inverters | INV3 | MCCB_ON | DI | NB03 AC MCCB 400A 36kA ON |  |  | PM-PVTX | Modbus RTU | 10009 | On state = 0 | 2
PV.INV3.P | PV Plant / Inverters | INV3 | P | AI | NB03 AC active power | kW |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30002
PV.INV3.Q | PV Plant / Inverters | INV3 | Q | AI | NB03 AC reactive power | kvar |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30004
PV.INV3.PF | PV Plant / Inverters | INV3 | PF | AI | NB03 power factor |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30006
PV.INV3.U_AC | PV Plant / Inverters | INV3 | U_AC | AI | NB03 AC voltage L-L | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30008
PV.INV3.I_AC | PV Plant / Inverters | INV3 | I_AC | AI | NB03 AC current | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30010
PV.INV3.F | PV Plant / Inverters | INV3 | F | AI | NB03 grid frequency | Hz |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30012
PV.INV3.P_DC | PV Plant / Inverters | INV3 | P_DC | AI | NB03 DC power | kW |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30014
PV.INV3.U_DC | PV Plant / Inverters | INV3 | U_DC | AI | NB03 DC bus voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30016
PV.INV3.T_INT | PV Plant / Inverters | INV3 | T_INT | AI | NB03 internal temperature | °C |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30018 | Limits | 1/2 |  |  | 70 | 80
PV.INV3.EFF | PV Plant / Inverters | INV3 | EFF | AI | NB03 conversion efficiency | % |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30020
PV.INV3.R_ISO | PV Plant / Inverters | INV3 | R_ISO | AI | NB03 insulation resistance | kΩ |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30022 | Limits | 1/2 |  | 200
PV.INV3.E_DAY | PV Plant / Inverters | INV3 | E_DAY | AI | NB03 energy today | kWh |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30024
PV.INV3.E_TOT | PV Plant / Inverters | INV3 | E_TOT | AI | NB03 energy total | MWh |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30026
PV.INV3.MPPT01_U | PV Plant / Inverters | INV3 | MPPT01_U | AI | NB03 MPPT1 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30028
PV.INV3.MPPT02_U | PV Plant / Inverters | INV3 | MPPT02_U | AI | NB03 MPPT2 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30030
PV.INV3.MPPT03_U | PV Plant / Inverters | INV3 | MPPT03_U | AI | NB03 MPPT3 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30032
PV.INV3.MPPT04_U | PV Plant / Inverters | INV3 | MPPT04_U | AI | NB03 MPPT4 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30034
PV.INV3.MPPT05_U | PV Plant / Inverters | INV3 | MPPT05_U | AI | NB03 MPPT5 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30036
PV.INV3.MPPT06_U | PV Plant / Inverters | INV3 | MPPT06_U | AI | NB03 MPPT6 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30038
PV.INV3.MPPT07_U | PV Plant / Inverters | INV3 | MPPT07_U | AI | NB03 MPPT7 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30040
PV.INV3.MPPT08_U | PV Plant / Inverters | INV3 | MPPT08_U | AI | NB03 MPPT8 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30042
PV.INV3.MPPT09_U | PV Plant / Inverters | INV3 | MPPT09_U | AI | NB03 MPPT9 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30044
PV.INV3.MPPT10_U | PV Plant / Inverters | INV3 | MPPT10_U | AI | NB03 MPPT10 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30046
PV.INV3.MPPT11_U | PV Plant / Inverters | INV3 | MPPT11_U | AI | NB03 MPPT11 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30048
PV.INV3.MPPT12_U | PV Plant / Inverters | INV3 | MPPT12_U | AI | NB03 MPPT12 voltage | V |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30050
PV.INV3.STR01_I | PV Plant / Inverters | INV3 | STR01_I | AI | NB03-01 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30052
PV.INV3.STR02_I | PV Plant / Inverters | INV3 | STR02_I | AI | NB03-02 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30054
PV.INV3.STR03_I | PV Plant / Inverters | INV3 | STR03_I | AI | NB03-03 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30056
PV.INV3.STR04_I | PV Plant / Inverters | INV3 | STR04_I | AI | NB03-04 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30058
PV.INV3.STR05_I | PV Plant / Inverters | INV3 | STR05_I | AI | NB03-05 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30060
PV.INV3.STR06_I | PV Plant / Inverters | INV3 | STR06_I | AI | NB03-06 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30062
PV.INV3.STR07_I | PV Plant / Inverters | INV3 | STR07_I | AI | NB03-07 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30064
PV.INV3.STR08_I | PV Plant / Inverters | INV3 | STR08_I | AI | NB03-08 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30066
PV.INV3.STR09_I | PV Plant / Inverters | INV3 | STR09_I | AI | NB03-09 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30068
PV.INV3.STR10_I | PV Plant / Inverters | INV3 | STR10_I | AI | NB03-10 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30070
PV.INV3.STR11_I | PV Plant / Inverters | INV3 | STR11_I | AI | NB03-11 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30072
PV.INV3.STR12_I | PV Plant / Inverters | INV3 | STR12_I | AI | NB03-12 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30074
PV.INV3.STR13_I | PV Plant / Inverters | INV3 | STR13_I | AI | NB03-13 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30076
PV.INV3.STR14_I | PV Plant / Inverters | INV3 | STR14_I | AI | NB03-14 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30078
PV.INV3.STR15_I | PV Plant / Inverters | INV3 | STR15_I | AI | NB03-15 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30080
PV.INV3.STR16_I | PV Plant / Inverters | INV3 | STR16_I | AI | NB03-16 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30082
PV.INV3.STR17_I | PV Plant / Inverters | INV3 | STR17_I | AI | NB03-17 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30084
PV.INV3.STR18_I | PV Plant / Inverters | INV3 | STR18_I | AI | NB03-18 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30086
PV.INV3.STR19_I | PV Plant / Inverters | INV3 | STR19_I | AI | NB03-19 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30088
PV.INV3.STR20_I | PV Plant / Inverters | INV3 | STR20_I | AI | NB03-20 string current (26 modules) | A |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30090
PV.INV3.CMD_START | PV Plant / Inverters | INV3 | CMD_START | DO | NB03 start / power on |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 1
PV.INV3.CMD_STOP | PV Plant / Inverters | INV3 | CMD_STOP | DO | NB03 stop / power off |  |  | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 2
PV.INV3.SP_PLIM | PV Plant / Inverters | INV3 | SP_PLIM | AO | NB03 active power limit | % | 0-100 | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 40002
PV.INV3.SP_PF | PV Plant / Inverters | INV3 | SP_PF | AO | NB03 power factor setpoint |  | 0.8i-0.8c | NB03 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 40004
PV.INV4.RUN | PV Plant / Inverters | INV4 | RUN | DI | NB04 running (grid-connected) |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10001
PV.INV4.STANDBY | PV Plant / Inverters | INV4 | STANDBY | DI | NB04 standby / derating |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10002
PV.INV4.FAULT | PV Plant / Inverters | INV4 | FAULT | DI | NB04 fault |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10003 | On state = 1 | 2
PV.INV4.COMM | PV Plant / Inverters | INV4 | COMM | DI | NB04 communication OK |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10004 | On state = 0 | 2
PV.INV4.ISO_FLT | PV Plant / Inverters | INV4 | ISO_FLT | DI | NB04 insulation (PV-earth) fault |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10005 | On state = 1 | 2
PV.INV4.DC_SPD | PV Plant / Inverters | INV4 | DC_SPD | DI | NB04 DC SPD failed |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10006 | On state = 1 | 3
PV.INV4.AC_SPD | PV Plant / Inverters | INV4 | AC_SPD | DI | NB04 AC SPD failed |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 10007 | On state = 1 | 3
PV.INV4.MCCB_ON | PV Plant / Inverters | INV4 | MCCB_ON | DI | NB04 AC MCCB 400A 36kA ON |  |  | PM-PVTX | Modbus RTU | 10010 | On state = 0 | 2
PV.INV4.P | PV Plant / Inverters | INV4 | P | AI | NB04 AC active power | kW |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30002
PV.INV4.Q | PV Plant / Inverters | INV4 | Q | AI | NB04 AC reactive power | kvar |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30004
PV.INV4.PF | PV Plant / Inverters | INV4 | PF | AI | NB04 power factor |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30006
PV.INV4.U_AC | PV Plant / Inverters | INV4 | U_AC | AI | NB04 AC voltage L-L | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30008
PV.INV4.I_AC | PV Plant / Inverters | INV4 | I_AC | AI | NB04 AC current | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30010
PV.INV4.F | PV Plant / Inverters | INV4 | F | AI | NB04 grid frequency | Hz |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30012
PV.INV4.P_DC | PV Plant / Inverters | INV4 | P_DC | AI | NB04 DC power | kW |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30014
PV.INV4.U_DC | PV Plant / Inverters | INV4 | U_DC | AI | NB04 DC bus voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30016
PV.INV4.T_INT | PV Plant / Inverters | INV4 | T_INT | AI | NB04 internal temperature | °C |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30018 | Limits | 1/2 |  |  | 70 | 80
PV.INV4.EFF | PV Plant / Inverters | INV4 | EFF | AI | NB04 conversion efficiency | % |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30020
PV.INV4.R_ISO | PV Plant / Inverters | INV4 | R_ISO | AI | NB04 insulation resistance | kΩ |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30022 | Limits | 1/2 |  | 200
PV.INV4.E_DAY | PV Plant / Inverters | INV4 | E_DAY | AI | NB04 energy today | kWh |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30024
PV.INV4.E_TOT | PV Plant / Inverters | INV4 | E_TOT | AI | NB04 energy total | MWh |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30026
PV.INV4.MPPT01_U | PV Plant / Inverters | INV4 | MPPT01_U | AI | NB04 MPPT1 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30028
PV.INV4.MPPT02_U | PV Plant / Inverters | INV4 | MPPT02_U | AI | NB04 MPPT2 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30030
PV.INV4.MPPT03_U | PV Plant / Inverters | INV4 | MPPT03_U | AI | NB04 MPPT3 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30032
PV.INV4.MPPT04_U | PV Plant / Inverters | INV4 | MPPT04_U | AI | NB04 MPPT4 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30034
PV.INV4.MPPT05_U | PV Plant / Inverters | INV4 | MPPT05_U | AI | NB04 MPPT5 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30036
PV.INV4.MPPT06_U | PV Plant / Inverters | INV4 | MPPT06_U | AI | NB04 MPPT6 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30038
PV.INV4.MPPT07_U | PV Plant / Inverters | INV4 | MPPT07_U | AI | NB04 MPPT7 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30040
PV.INV4.MPPT08_U | PV Plant / Inverters | INV4 | MPPT08_U | AI | NB04 MPPT8 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30042
PV.INV4.MPPT09_U | PV Plant / Inverters | INV4 | MPPT09_U | AI | NB04 MPPT9 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30044
PV.INV4.MPPT10_U | PV Plant / Inverters | INV4 | MPPT10_U | AI | NB04 MPPT10 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30046
PV.INV4.MPPT11_U | PV Plant / Inverters | INV4 | MPPT11_U | AI | NB04 MPPT11 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30048
PV.INV4.MPPT12_U | PV Plant / Inverters | INV4 | MPPT12_U | AI | NB04 MPPT12 voltage | V |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30050
PV.INV4.STR01_I | PV Plant / Inverters | INV4 | STR01_I | AI | NB04-01 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30052
PV.INV4.STR02_I | PV Plant / Inverters | INV4 | STR02_I | AI | NB04-02 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30054
PV.INV4.STR03_I | PV Plant / Inverters | INV4 | STR03_I | AI | NB04-03 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30056
PV.INV4.STR04_I | PV Plant / Inverters | INV4 | STR04_I | AI | NB04-04 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30058
PV.INV4.STR05_I | PV Plant / Inverters | INV4 | STR05_I | AI | NB04-05 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30060
PV.INV4.STR06_I | PV Plant / Inverters | INV4 | STR06_I | AI | NB04-06 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30062
PV.INV4.STR07_I | PV Plant / Inverters | INV4 | STR07_I | AI | NB04-07 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30064
PV.INV4.STR08_I | PV Plant / Inverters | INV4 | STR08_I | AI | NB04-08 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30066
PV.INV4.STR09_I | PV Plant / Inverters | INV4 | STR09_I | AI | NB04-09 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30068
PV.INV4.STR10_I | PV Plant / Inverters | INV4 | STR10_I | AI | NB04-10 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30070
PV.INV4.STR11_I | PV Plant / Inverters | INV4 | STR11_I | AI | NB04-11 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30072
PV.INV4.STR12_I | PV Plant / Inverters | INV4 | STR12_I | AI | NB04-12 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30074
PV.INV4.STR13_I | PV Plant / Inverters | INV4 | STR13_I | AI | NB04-13 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30076
PV.INV4.STR14_I | PV Plant / Inverters | INV4 | STR14_I | AI | NB04-14 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30078
PV.INV4.STR15_I | PV Plant / Inverters | INV4 | STR15_I | AI | NB04-15 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30080
PV.INV4.STR16_I | PV Plant / Inverters | INV4 | STR16_I | AI | NB04-16 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30082
PV.INV4.STR17_I | PV Plant / Inverters | INV4 | STR17_I | AI | NB04-17 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30084
PV.INV4.STR18_I | PV Plant / Inverters | INV4 | STR18_I | AI | NB04-18 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30086
PV.INV4.STR19_I | PV Plant / Inverters | INV4 | STR19_I | AI | NB04-19 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30088
PV.INV4.STR20_I | PV Plant / Inverters | INV4 | STR20_I | AI | NB04-20 string current (26 modules) | A |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 30090
PV.INV4.CMD_START | PV Plant / Inverters | INV4 | CMD_START | DO | NB04 start / power on |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 1
PV.INV4.CMD_STOP | PV Plant / Inverters | INV4 | CMD_STOP | DO | NB04 stop / power off |  |  | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 2
PV.INV4.SP_PLIM | PV Plant / Inverters | INV4 | SP_PLIM | AO | NB04 active power limit | % | 0-100 | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 40002
PV.INV4.SP_PF | PV Plant / Inverters | INV4 | SP_PF | AO | NB04 power factor setpoint |  | 0.8i-0.8c | NB04 | Power-line carrier (PLC) over AC cables → PLC box → Ethernet / Modbus TCP | 40004
MET.WS.IRR_POA | Weather Station | WS | IRR_POA | AI | Plane-of-array irradiance (SMP12-A) | W/m² |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 30002
MET.WS.IRR_GHI | Weather Station | WS | IRR_GHI | AI | Global horizontal irradiance | W/m² |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 30004
MET.WS.WIND_SPD | Weather Station | WS | WIND_SPD | AI | Wind speed (Gill WindSonic) | m/s |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 30006 | Limits | 1/2 |  |  | 20 | 25
MET.WS.WIND_DIR | Weather Station | WS | WIND_DIR | AI | Wind direction | ° |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 30008
MET.WS.T_AMB | Weather Station | WS | T_AMB | AI | Ambient temperature | °C |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 30010
MET.WS.T_MOD | Weather Station | WS | T_MOD | AI | Module temperature | °C |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 30012
MET.WS.HUM | Weather Station | WS | HUM | AI | Relative humidity | % |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 30014
MET.WS.INSOL_DAY | Weather Station | WS | INSOL_DAY | AI | Insolation today | kWh/m² |  | SCADA | Calculated
MET.WS.PR | Weather Station | WS | PR | AI | Performance ratio (instant) | % |  | SCADA | Calculated
MET.WS.COMM | Weather Station | WS | COMM | DI | Weather station communication OK |  |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 10001 | On state = 0 | 3
MET.WS.SENSOR_FLT | Weather Station | WS | SENSOR_FLT | DI | Sensor out of range / fault |  |  | BLUELOG | blue'Log Fieldbus Ext / Modbus TCP | 10002 | On state = 1 | 3
BESS.SYS.SOC | Battery Energy Storage | SYS | SOC | AI | Battery state of charge | % |  | EMS-BESS | Modbus TCP | 30002 | Limits | 1/2 | 10 | 20 | 99
BESS.SYS.SOH | Battery Energy Storage | SYS | SOH | AI | Battery state of health | % |  | EMS-BESS | Modbus TCP | 30004 | Limits | 1/2 |  | 80
BESS.SYS.E_AVAIL | Battery Energy Storage | SYS | E_AVAIL | AI | Available energy | kWh |  | EMS-BESS | Modbus TCP | 30006
BESS.SYS.P | Battery Energy Storage | SYS | P | AI | BESS active power (+discharge / -charge) | kW |  | EMS-BESS | Modbus TCP | 30008
BESS.SYS.Q | Battery Energy Storage | SYS | Q | AI | BESS reactive power | kvar |  | EMS-BESS | Modbus TCP | 30010
BESS.SYS.P_CHG_MAX | Battery Energy Storage | SYS | P_CHG_MAX | AI | Allowable charge power | kW |  | EMS-BESS | Modbus TCP | 30012
BESS.SYS.P_DIS_MAX | Battery Energy Storage | SYS | P_DIS_MAX | AI | Allowable discharge power | kW |  | EMS-BESS | Modbus TCP | 30014
BESS.SYS.U_DC | Battery Energy Storage | SYS | U_DC | AI | Battery DC voltage | V |  | EMS-BESS | Modbus TCP | 30016
BESS.SYS.I_DC | Battery Energy Storage | SYS | I_DC | AI | Battery DC current | A |  | EMS-BESS | Modbus TCP | 30018
BESS.SYS.T_CELL_MAX | Battery Energy Storage | SYS | T_CELL_MAX | AI | Max cell temperature | °C |  | EMS-BESS | Modbus TCP | 30020 | Limits | 1/2 |  |  | 45 | 55
BESS.SYS.T_CELL_MIN | Battery Energy Storage | SYS | T_CELL_MIN | AI | Min cell temperature | °C |  | EMS-BESS | Modbus TCP | 30022 | Limits | 1/2 |  | 5
BESS.SYS.U_CELL_MAX | Battery Energy Storage | SYS | U_CELL_MAX | AI | Max cell voltage | V |  | EMS-BESS | Modbus TCP | 30024 | Limits | 1/2 |  |  | 3.6 | 3.65
BESS.SYS.U_CELL_MIN | Battery Energy Storage | SYS | U_CELL_MIN | AI | Min cell voltage | V |  | EMS-BESS | Modbus TCP | 30026 | Limits | 1/2 | 2.6 | 2.9
BESS.SYS.E_CHG | Battery Energy Storage | SYS | E_CHG | AI | Energy charged total | MWh |  | EMS-BESS | Modbus TCP | 30028
BESS.SYS.E_DIS | Battery Energy Storage | SYS | E_DIS | AI | Energy discharged total | MWh |  | EMS-BESS | Modbus TCP | 30030
BESS.SYS.CYCLES | Battery Energy Storage | SYS | CYCLES | AI | Equivalent full cycles |  |  | EMS-BESS | Modbus TCP | 30032
BESS.SYS.GRID_FORMING | Battery Energy Storage | SYS | GRID_FORMING | DI | BESS operating grid-forming (VSG) |  |  | EMS-BESS | Modbus TCP | 10001
BESS.SYS.BMS_FAULT | Battery Energy Storage | SYS | BMS_FAULT | DI | BMS fault |  |  | EMS-BESS | Modbus TCP | 10002 | On state = 1 | 1
BESS.SYS.BMS_WARN | Battery Energy Storage | SYS | BMS_WARN | DI | BMS warning |  |  | EMS-BESS | Modbus TCP | 10003 | On state = 1 | 3
BESS.SYS.ESD | Battery Energy Storage | SYS | ESD | DI | BESS emergency stop activated |  |  | EMS-BESS | Modbus TCP | 10004 | On state = 1 | 1
BESS.SYS.DOOR | Battery Energy Storage | SYS | DOOR | DI | ESS cabin door open |  |  | EMS-BESS | Modbus TCP | 10005 | On state = 1 | 4
BESS.SYS.CMD_MODE | Battery Energy Storage | SYS | CMD_MODE | AO | BESS operating mode (0 stop, 1 grid-forming, 2 grid-following P/Q) |  | 0-2 | EMS-BESS | Modbus TCP | 40002
BESS.SYS.SP_P | Battery Energy Storage | SYS | SP_P | AO | Active power setpoint (grid-following) | kW | -950..950 | EMS-BESS | Modbus TCP | 40004
BESS.SYS.SP_F | Battery Energy Storage | SYS | SP_F | AO | Frequency setpoint (grid-forming) | Hz | 49.5-50.5 | EMS-BESS | Modbus TCP | 40006
BESS.SYS.SP_U | Battery Energy Storage | SYS | SP_U | AO | Voltage setpoint (grid-forming) | V | 621-759 | EMS-BESS | Modbus TCP | 40008
BESS.SYS.CMD_START | Battery Energy Storage | SYS | CMD_START | DO | BESS start |  |  | EMS-BESS | Modbus TCP | 1
BESS.SYS.CMD_STOP | Battery Energy Storage | SYS | CMD_STOP | DO | BESS stop |  |  | EMS-BESS | Modbus TCP | 2
BESS.SYS.CMD_RESET | Battery Energy Storage | SYS | CMD_RESET | DO | BESS fault reset |  |  | EMS-BESS | Modbus TCP | 3
BESS.LV_ACB.CB_CLOSED | Battery Energy Storage | LV_ACB | CB_CLOSED | DI | BESS LV ACB 1000A closed |  |  | PM-BESSTX | Modbus RTU | 10001
BESS.LV_ACB.CB_OPEN | Battery Energy Storage | LV_ACB | CB_OPEN | DI | BESS LV ACB 1000A open |  |  | PM-BESSTX | Modbus RTU | 10002
BESS.LV_ACB.CB_TRIPPED | Battery Energy Storage | LV_ACB | CB_TRIPPED | DI | BESS LV ACB 1000A tripped (protection) |  |  | PM-BESSTX | Modbus RTU | 10003 | On state = 1 | 1
BESS.LV_ACB.CB_SPRING | Battery Energy Storage | LV_ACB | CB_SPRING | DI | BESS LV ACB 1000A spring charged |  |  | PM-BESSTX | Modbus RTU | 10004 | On state = 0 | 3
BESS.LV_ACB.CB_RACKED | Battery Energy Storage | LV_ACB | CB_RACKED | DI | BESS LV ACB 1000A racked-in / service position |  |  | PM-BESSTX | Modbus RTU | 10005
BESS.LV_ACB.LR_REMOTE | Battery Energy Storage | LV_ACB | LR_REMOTE | DI | Local/Remote switch in REMOTE |  |  | PM-BESSTX | Modbus RTU | 10006 | On state = 0 | 4
BESS.LV_ACB.CMD_OPEN | Battery Energy Storage | LV_ACB | CMD_OPEN | DO | BESS LV ACB 1000A open command |  |  | PM-BESSTX | Modbus RTU | 1
BESS.LV_ACB.CMD_CLOSE | Battery Energy Storage | LV_ACB | CMD_CLOSE | DO | BESS LV ACB 1000A close command |  |  | PM-BESSTX | Modbus RTU | 2
BESS.POC.I_L1 | Battery Energy Storage | POC | I_L1 | AI | Current L1 | A |  | PM-BESSTX | Modbus RTU | 30002
BESS.POC.I_L2 | Battery Energy Storage | POC | I_L2 | AI | Current L2 | A |  | PM-BESSTX | Modbus RTU | 30004
BESS.POC.I_L3 | Battery Energy Storage | POC | I_L3 | AI | Current L3 | A |  | PM-BESSTX | Modbus RTU | 30006
BESS.POC.U_L12 | Battery Energy Storage | POC | U_L12 | AI | Voltage L12 | V |  | PM-BESSTX | Modbus RTU | 30008
BESS.POC.U_L23 | Battery Energy Storage | POC | U_L23 | AI | Voltage L23 | V |  | PM-BESSTX | Modbus RTU | 30010
BESS.POC.U_L31 | Battery Energy Storage | POC | U_L31 | AI | Voltage L31 | V |  | PM-BESSTX | Modbus RTU | 30012
BESS.POC.P | Battery Energy Storage | POC | P | AI | Active power | kW |  | PM-BESSTX | Modbus RTU | 30014
BESS.POC.Q | Battery Energy Storage | POC | Q | AI | Reactive power | kvar |  | PM-BESSTX | Modbus RTU | 30016
BESS.POC.S | Battery Energy Storage | POC | S | AI | Apparent power | kVA |  | PM-BESSTX | Modbus RTU | 30018
BESS.POC.PF | Battery Energy Storage | POC | PF | AI | Power factor |  |  | PM-BESSTX | Modbus RTU | 30020
BESS.POC.F | Battery Energy Storage | POC | F | AI | Frequency | Hz |  | PM-BESSTX | Modbus RTU | 30022 | Limits | 1/2 | 47.5 | 49.5 | 50.5 | 51.5
BESS.POC.E_IMP | Battery Energy Storage | POC | E_IMP | AI | Active energy import | MWh |  | PM-BESSTX | Modbus RTU | 30024
BESS.POC.E_EXP | Battery Energy Storage | POC | E_EXP | AI | Active energy export | MWh |  | PM-BESSTX | Modbus RTU | 30026
BESS.POC.THD_U | Battery Energy Storage | POC | THD_U | AI | Voltage THD | % |  | PM-BESSTX | Modbus RTU | 30028 | Limits | 1/2 |  |  | 5 | 8
BESS.PCS1.RUN | Battery Energy Storage | PCS1 | RUN | DI | PCS Unit 1# running |  |  | PCS-1 | Modbus TCP | 10001
BESS.PCS1.FAULT | Battery Energy Storage | PCS1 | FAULT | DI | PCS Unit 1# fault |  |  | PCS-1 | Modbus TCP | 10002 | On state = 1 | 1
BESS.PCS1.ACB_CLOSED | Battery Energy Storage | PCS1 | ACB_CLOSED | DI | PCS Unit 1# 400A breaker closed |  |  | PCS-1 | Modbus TCP | 10003
BESS.PCS1.DC_SW | Battery Energy Storage | PCS1 | DC_SW | DI | PCS Unit 1# DC switch closed |  |  | PCS-1 | Modbus TCP | 10004
BESS.PCS1.P | Battery Energy Storage | PCS1 | P | AI | PCS Unit 1# active power | kW |  | PCS-1 | Modbus TCP | 30002
BESS.PCS1.Q | Battery Energy Storage | PCS1 | Q | AI | PCS Unit 1# reactive power | kvar |  | PCS-1 | Modbus TCP | 30004
BESS.PCS1.U_AC | Battery Energy Storage | PCS1 | U_AC | AI | PCS Unit 1# AC voltage | V |  | PCS-1 | Modbus TCP | 30006
BESS.PCS1.I_AC | Battery Energy Storage | PCS1 | I_AC | AI | PCS Unit 1# AC current | A |  | PCS-1 | Modbus TCP | 30008
BESS.PCS1.U_DC | Battery Energy Storage | PCS1 | U_DC | AI | PCS Unit 1# DC voltage | V |  | PCS-1 | Modbus TCP | 30010
BESS.PCS1.T_IGBT | Battery Energy Storage | PCS1 | T_IGBT | AI | PCS Unit 1# IGBT temperature | °C |  | PCS-1 | Modbus TCP | 30012 | Limits | 1/2 |  |  | 75 | 85
BESS.PCS2.RUN | Battery Energy Storage | PCS2 | RUN | DI | PCS Unit 2# running |  |  | PCS-2 | Modbus TCP | 10001
BESS.PCS2.FAULT | Battery Energy Storage | PCS2 | FAULT | DI | PCS Unit 2# fault |  |  | PCS-2 | Modbus TCP | 10002 | On state = 1 | 1
BESS.PCS2.ACB_CLOSED | Battery Energy Storage | PCS2 | ACB_CLOSED | DI | PCS Unit 2# 400A breaker closed |  |  | PCS-2 | Modbus TCP | 10003
BESS.PCS2.DC_SW | Battery Energy Storage | PCS2 | DC_SW | DI | PCS Unit 2# DC switch closed |  |  | PCS-2 | Modbus TCP | 10004
BESS.PCS2.P | Battery Energy Storage | PCS2 | P | AI | PCS Unit 2# active power | kW |  | PCS-2 | Modbus TCP | 30002
BESS.PCS2.Q | Battery Energy Storage | PCS2 | Q | AI | PCS Unit 2# reactive power | kvar |  | PCS-2 | Modbus TCP | 30004
BESS.PCS2.U_AC | Battery Energy Storage | PCS2 | U_AC | AI | PCS Unit 2# AC voltage | V |  | PCS-2 | Modbus TCP | 30006
BESS.PCS2.I_AC | Battery Energy Storage | PCS2 | I_AC | AI | PCS Unit 2# AC current | A |  | PCS-2 | Modbus TCP | 30008
BESS.PCS2.U_DC | Battery Energy Storage | PCS2 | U_DC | AI | PCS Unit 2# DC voltage | V |  | PCS-2 | Modbus TCP | 30010
BESS.PCS2.T_IGBT | Battery Energy Storage | PCS2 | T_IGBT | AI | PCS Unit 2# IGBT temperature | °C |  | PCS-2 | Modbus TCP | 30012 | Limits | 1/2 |  |  | 75 | 85
BESS.RACK1.SOC | Battery Energy Storage | RACK1 | SOC | AI | Rack 1 SOC | % |  | BMS-R1 | Modbus TCP | 30002
BESS.RACK1.U | Battery Energy Storage | RACK1 | U | AI | Rack 1 voltage | V |  | BMS-R1 | Modbus TCP | 30004
BESS.RACK1.I | Battery Energy Storage | RACK1 | I | AI | Rack 1 current | A |  | BMS-R1 | Modbus TCP | 30006
BESS.RACK1.T_MAX | Battery Energy Storage | RACK1 | T_MAX | AI | Rack 1 max cell temperature | °C |  | BMS-R1 | Modbus TCP | 30008 | Limits | 1/2 |  |  | 45 | 55
BESS.RACK1.U_CMAX | Battery Energy Storage | RACK1 | U_CMAX | AI | Rack 1 max cell voltage | V |  | BMS-R1 | Modbus TCP | 30010
BESS.RACK1.U_CMIN | Battery Energy Storage | RACK1 | U_CMIN | AI | Rack 1 min cell voltage | V |  | BMS-R1 | Modbus TCP | 30012
BESS.RACK1.CONTACTOR | Battery Energy Storage | RACK1 | CONTACTOR | DI | Rack 1 main contactor closed |  |  | BMS-R1 | Modbus TCP | 10001 | On state = 0 | 2
BESS.RACK1.FAULT | Battery Energy Storage | RACK1 | FAULT | DI | Rack 1 fault |  |  | BMS-R1 | Modbus TCP | 10002 | On state = 1 | 2
BESS.RACK2.SOC | Battery Energy Storage | RACK2 | SOC | AI | Rack 2 SOC | % |  | BMS-R2 | Modbus TCP | 30002
BESS.RACK2.U | Battery Energy Storage | RACK2 | U | AI | Rack 2 voltage | V |  | BMS-R2 | Modbus TCP | 30004
BESS.RACK2.I | Battery Energy Storage | RACK2 | I | AI | Rack 2 current | A |  | BMS-R2 | Modbus TCP | 30006
BESS.RACK2.T_MAX | Battery Energy Storage | RACK2 | T_MAX | AI | Rack 2 max cell temperature | °C |  | BMS-R2 | Modbus TCP | 30008 | Limits | 1/2 |  |  | 45 | 55
BESS.RACK2.U_CMAX | Battery Energy Storage | RACK2 | U_CMAX | AI | Rack 2 max cell voltage | V |  | BMS-R2 | Modbus TCP | 30010
BESS.RACK2.U_CMIN | Battery Energy Storage | RACK2 | U_CMIN | AI | Rack 2 min cell voltage | V |  | BMS-R2 | Modbus TCP | 30012
BESS.RACK2.CONTACTOR | Battery Energy Storage | RACK2 | CONTACTOR | DI | Rack 2 main contactor closed |  |  | BMS-R2 | Modbus TCP | 10001 | On state = 0 | 2
BESS.RACK2.FAULT | Battery Energy Storage | RACK2 | FAULT | DI | Rack 2 fault |  |  | BMS-R2 | Modbus TCP | 10002 | On state = 1 | 2
BESS.RACK3.SOC | Battery Energy Storage | RACK3 | SOC | AI | Rack 3 SOC | % |  | BMS-R3 | Modbus TCP | 30002
BESS.RACK3.U | Battery Energy Storage | RACK3 | U | AI | Rack 3 voltage | V |  | BMS-R3 | Modbus TCP | 30004
BESS.RACK3.I | Battery Energy Storage | RACK3 | I | AI | Rack 3 current | A |  | BMS-R3 | Modbus TCP | 30006
BESS.RACK3.T_MAX | Battery Energy Storage | RACK3 | T_MAX | AI | Rack 3 max cell temperature | °C |  | BMS-R3 | Modbus TCP | 30008 | Limits | 1/2 |  |  | 45 | 55
BESS.RACK3.U_CMAX | Battery Energy Storage | RACK3 | U_CMAX | AI | Rack 3 max cell voltage | V |  | BMS-R3 | Modbus TCP | 30010
BESS.RACK3.U_CMIN | Battery Energy Storage | RACK3 | U_CMIN | AI | Rack 3 min cell voltage | V |  | BMS-R3 | Modbus TCP | 30012
BESS.RACK3.CONTACTOR | Battery Energy Storage | RACK3 | CONTACTOR | DI | Rack 3 main contactor closed |  |  | BMS-R3 | Modbus TCP | 10001 | On state = 0 | 2
BESS.RACK3.FAULT | Battery Energy Storage | RACK3 | FAULT | DI | Rack 3 fault |  |  | BMS-R3 | Modbus TCP | 10002 | On state = 1 | 2
BESS.RACK4.SOC | Battery Energy Storage | RACK4 | SOC | AI | Rack 4 SOC | % |  | BMS-R4 | Modbus TCP | 30002
BESS.RACK4.U | Battery Energy Storage | RACK4 | U | AI | Rack 4 voltage | V |  | BMS-R4 | Modbus TCP | 30004
BESS.RACK4.I | Battery Energy Storage | RACK4 | I | AI | Rack 4 current | A |  | BMS-R4 | Modbus TCP | 30006
BESS.RACK4.T_MAX | Battery Energy Storage | RACK4 | T_MAX | AI | Rack 4 max cell temperature | °C |  | BMS-R4 | Modbus TCP | 30008 | Limits | 1/2 |  |  | 45 | 55
BESS.RACK4.U_CMAX | Battery Energy Storage | RACK4 | U_CMAX | AI | Rack 4 max cell voltage | V |  | BMS-R4 | Modbus TCP | 30010
BESS.RACK4.U_CMIN | Battery Energy Storage | RACK4 | U_CMIN | AI | Rack 4 min cell voltage | V |  | BMS-R4 | Modbus TCP | 30012
BESS.RACK4.CONTACTOR | Battery Energy Storage | RACK4 | CONTACTOR | DI | Rack 4 main contactor closed |  |  | BMS-R4 | Modbus TCP | 10001 | On state = 0 | 2
BESS.RACK4.FAULT | Battery Energy Storage | RACK4 | FAULT | DI | Rack 4 fault |  |  | BMS-R4 | Modbus TCP | 10002 | On state = 1 | 2
BESS.RACK5.SOC | Battery Energy Storage | RACK5 | SOC | AI | Rack 5 SOC | % |  | BMS-R5 | Modbus TCP | 30002
BESS.RACK5.U | Battery Energy Storage | RACK5 | U | AI | Rack 5 voltage | V |  | BMS-R5 | Modbus TCP | 30004
BESS.RACK5.I | Battery Energy Storage | RACK5 | I | AI | Rack 5 current | A |  | BMS-R5 | Modbus TCP | 30006
BESS.RACK5.T_MAX | Battery Energy Storage | RACK5 | T_MAX | AI | Rack 5 max cell temperature | °C |  | BMS-R5 | Modbus TCP | 30008 | Limits | 1/2 |  |  | 45 | 55
BESS.RACK5.U_CMAX | Battery Energy Storage | RACK5 | U_CMAX | AI | Rack 5 max cell voltage | V |  | BMS-R5 | Modbus TCP | 30010
BESS.RACK5.U_CMIN | Battery Energy Storage | RACK5 | U_CMIN | AI | Rack 5 min cell voltage | V |  | BMS-R5 | Modbus TCP | 30012
BESS.RACK5.CONTACTOR | Battery Energy Storage | RACK5 | CONTACTOR | DI | Rack 5 main contactor closed |  |  | BMS-R5 | Modbus TCP | 10001 | On state = 0 | 2
BESS.RACK5.FAULT | Battery Energy Storage | RACK5 | FAULT | DI | Rack 5 fault |  |  | BMS-R5 | Modbus TCP | 10002 | On state = 1 | 2
BESS.RACK6.SOC | Battery Energy Storage | RACK6 | SOC | AI | Rack 6 SOC | % |  | BMS-R6 | Modbus TCP | 30002
BESS.RACK6.U | Battery Energy Storage | RACK6 | U | AI | Rack 6 voltage | V |  | BMS-R6 | Modbus TCP | 30004
BESS.RACK6.I | Battery Energy Storage | RACK6 | I | AI | Rack 6 current | A |  | BMS-R6 | Modbus TCP | 30006
BESS.RACK6.T_MAX | Battery Energy Storage | RACK6 | T_MAX | AI | Rack 6 max cell temperature | °C |  | BMS-R6 | Modbus TCP | 30008 | Limits | 1/2 |  |  | 45 | 55
BESS.RACK6.U_CMAX | Battery Energy Storage | RACK6 | U_CMAX | AI | Rack 6 max cell voltage | V |  | BMS-R6 | Modbus TCP | 30010
BESS.RACK6.U_CMIN | Battery Energy Storage | RACK6 | U_CMIN | AI | Rack 6 min cell voltage | V |  | BMS-R6 | Modbus TCP | 30012
BESS.RACK6.CONTACTOR | Battery Energy Storage | RACK6 | CONTACTOR | DI | Rack 6 main contactor closed |  |  | BMS-R6 | Modbus TCP | 10001 | On state = 0 | 2
BESS.RACK6.FAULT | Battery Energy Storage | RACK6 | FAULT | DI | Rack 6 fault |  |  | BMS-R6 | Modbus TCP | 10002 | On state = 1 | 2
BESS.RACK7.SOC | Battery Energy Storage | RACK7 | SOC | AI | Rack 7 SOC | % |  | BMS-R7 | Modbus TCP | 30002
BESS.RACK7.U | Battery Energy Storage | RACK7 | U | AI | Rack 7 voltage | V |  | BMS-R7 | Modbus TCP | 30004
BESS.RACK7.I | Battery Energy Storage | RACK7 | I | AI | Rack 7 current | A |  | BMS-R7 | Modbus TCP | 30006
BESS.RACK7.T_MAX | Battery Energy Storage | RACK7 | T_MAX | AI | Rack 7 max cell temperature | °C |  | BMS-R7 | Modbus TCP | 30008 | Limits | 1/2 |  |  | 45 | 55
BESS.RACK7.U_CMAX | Battery Energy Storage | RACK7 | U_CMAX | AI | Rack 7 max cell voltage | V |  | BMS-R7 | Modbus TCP | 30010
BESS.RACK7.U_CMIN | Battery Energy Storage | RACK7 | U_CMIN | AI | Rack 7 min cell voltage | V |  | BMS-R7 | Modbus TCP | 30012
BESS.RACK7.CONTACTOR | Battery Energy Storage | RACK7 | CONTACTOR | DI | Rack 7 main contactor closed |  |  | BMS-R7 | Modbus TCP | 10001 | On state = 0 | 2
BESS.RACK7.FAULT | Battery Energy Storage | RACK7 | FAULT | DI | Rack 7 fault |  |  | BMS-R7 | Modbus TCP | 10002 | On state = 1 | 2
BESS.RACK8.SOC | Battery Energy Storage | RACK8 | SOC | AI | Rack 8 SOC | % |  | BMS-R8 | Modbus TCP | 30002
BESS.RACK8.U | Battery Energy Storage | RACK8 | U | AI | Rack 8 voltage | V |  | BMS-R8 | Modbus TCP | 30004
BESS.RACK8.I | Battery Energy Storage | RACK8 | I | AI | Rack 8 current | A |  | BMS-R8 | Modbus TCP | 30006
BESS.RACK8.T_MAX | Battery Energy Storage | RACK8 | T_MAX | AI | Rack 8 max cell temperature | °C |  | BMS-R8 | Modbus TCP | 30008 | Limits | 1/2 |  |  | 45 | 55
BESS.RACK8.U_CMAX | Battery Energy Storage | RACK8 | U_CMAX | AI | Rack 8 max cell voltage | V |  | BMS-R8 | Modbus TCP | 30010
BESS.RACK8.U_CMIN | Battery Energy Storage | RACK8 | U_CMIN | AI | Rack 8 min cell voltage | V |  | BMS-R8 | Modbus TCP | 30012
BESS.RACK8.CONTACTOR | Battery Energy Storage | RACK8 | CONTACTOR | DI | Rack 8 main contactor closed |  |  | BMS-R8 | Modbus TCP | 10001 | On state = 0 | 2
BESS.RACK8.FAULT | Battery Energy Storage | RACK8 | FAULT | DI | Rack 8 fault |  |  | BMS-R8 | Modbus TCP | 10002 | On state = 1 | 2
BESS.HVAC.T_CABIN | Battery Energy Storage | HVAC | T_CABIN | AI | ESS cabin air temperature | °C |  | EMS-BESS | Modbus TCP | 30034 | Limits | 1/2 |  |  | 30 | 35
BESS.HVAC.HUM | Battery Energy Storage | HVAC | HUM | AI | ESS cabin humidity | % |  | EMS-BESS | Modbus TCP | 30036 | Limits | 1/2 |  |  | 85
BESS.HVAC.RUN | Battery Energy Storage | HVAC | RUN | DI | HVAC / liquid cooling running |  |  | EMS-BESS | Modbus TCP | 10006
BESS.HVAC.FAULT | Battery Energy Storage | HVAC | FAULT | DI | HVAC / chiller fault |  |  | EMS-BESS | Modbus TCP | 10007 | On state = 1 | 2
FIRE.FZ_BESS.PRE_ALM | Fire Detection & Suppression | FZ_BESS | PRE_ALM | DI | BESS / ESS Cabin pre-alarm (1st detector) |  |  | FACP | Modbus TCP / dry contacts | 10001 | On state = 1 | 2
FIRE.FZ_BESS.FIRE | Fire Detection & Suppression | FZ_BESS | FIRE | DI | BESS / ESS Cabin FIRE alarm (confirmed) |  |  | FACP | Modbus TCP / dry contacts | 10002 | On state = 1 | 1
FIRE.FZ_BESS.FAULT | Fire Detection & Suppression | FZ_BESS | FAULT | DI | BESS / ESS Cabin detection loop fault |  |  | FACP | Modbus TCP / dry contacts | 10003 | On state = 1 | 3
FIRE.FZ_BESS.DISABLED | Fire Detection & Suppression | FZ_BESS | DISABLED | DI | BESS / ESS Cabin zone disabled / isolated |  |  | FACP | Modbus TCP / dry contacts | 10004 | On state = 1 | 3
FIRE.FZ_BESS.REL_PENDING | Fire Detection & Suppression | FZ_BESS | REL_PENDING | DI | BESS / ESS Cabin extinguishant release countdown |  |  | FACP | Modbus TCP / dry contacts | 10005 | On state = 1 | 1
FIRE.FZ_BESS.RELEASED | Fire Detection & Suppression | FZ_BESS | RELEASED | DI | BESS / ESS Cabin extinguishant released |  |  | FACP | Modbus TCP / dry contacts | 10006 | On state = 1 | 1
FIRE.FZ_BESS.MAN_INHIBIT | Fire Detection & Suppression | FZ_BESS | MAN_INHIBIT | DI | BESS / ESS Cabin manual / auto inhibit selected |  |  | FACP | Modbus TCP / dry contacts | 10007 | On state = 1 | 3
FIRE.FZ_BESS.CYL_LOW | Fire Detection & Suppression | FZ_BESS | CYL_LOW | DI | BESS / ESS Cabin agent cylinder pressure low |  |  | FACP | Modbus TCP / dry contacts | 10008 | On state = 1 | 2
FIRE.FZ_BESS.GAS_H2 | Fire Detection & Suppression | FZ_BESS | GAS_H2 | AI | ESS cabin H2 concentration | %LEL |  | FACP | Modbus TCP / dry contacts | 30002 | Limits | 1/2 |  |  | 10 | 25
FIRE.FZ_BESS.GAS_CO | Fire Detection & Suppression | FZ_BESS | GAS_CO | AI | ESS cabin CO concentration | ppm |  | FACP | Modbus TCP / dry contacts | 30004 | Limits | 1/2 |  |  | 50 | 150
FIRE.FZ_BESS.VENT_RUN | Fire Detection & Suppression | FZ_BESS | VENT_RUN | DI | ESS exhaust / explosion venting fan running |  |  | FACP | Modbus TCP / dry contacts | 10009
FIRE.FZ_GIS.PRE_ALM | Fire Detection & Suppression | FZ_GIS | PRE_ALM | DI | 11kV GIS Room pre-alarm (1st detector) |  |  | FACP | Modbus TCP / dry contacts | 10010 | On state = 1 | 2
FIRE.FZ_GIS.FIRE | Fire Detection & Suppression | FZ_GIS | FIRE | DI | 11kV GIS Room FIRE alarm (confirmed) |  |  | FACP | Modbus TCP / dry contacts | 10011 | On state = 1 | 1
FIRE.FZ_GIS.FAULT | Fire Detection & Suppression | FZ_GIS | FAULT | DI | 11kV GIS Room detection loop fault |  |  | FACP | Modbus TCP / dry contacts | 10012 | On state = 1 | 3
FIRE.FZ_GIS.DISABLED | Fire Detection & Suppression | FZ_GIS | DISABLED | DI | 11kV GIS Room zone disabled / isolated |  |  | FACP | Modbus TCP / dry contacts | 10013 | On state = 1 | 3
FIRE.FZ_GIS.REL_PENDING | Fire Detection & Suppression | FZ_GIS | REL_PENDING | DI | 11kV GIS Room extinguishant release countdown |  |  | FACP | Modbus TCP / dry contacts | 10014 | On state = 1 | 1
FIRE.FZ_GIS.RELEASED | Fire Detection & Suppression | FZ_GIS | RELEASED | DI | 11kV GIS Room extinguishant released |  |  | FACP | Modbus TCP / dry contacts | 10015 | On state = 1 | 1
FIRE.FZ_GIS.MAN_INHIBIT | Fire Detection & Suppression | FZ_GIS | MAN_INHIBIT | DI | 11kV GIS Room manual / auto inhibit selected |  |  | FACP | Modbus TCP / dry contacts | 10016 | On state = 1 | 3
FIRE.FZ_GIS.CYL_LOW | Fire Detection & Suppression | FZ_GIS | CYL_LOW | DI | 11kV GIS Room agent cylinder pressure low |  |  | FACP | Modbus TCP / dry contacts | 10017 | On state = 1 | 2
FIRE.FZ_INV.PRE_ALM | Fire Detection & Suppression | FZ_INV | PRE_ALM | DI | Inverter / PV TX Station pre-alarm (1st detector) |  |  | FACP | Modbus TCP / dry contacts | 10018 | On state = 1 | 2
FIRE.FZ_INV.FIRE | Fire Detection & Suppression | FZ_INV | FIRE | DI | Inverter / PV TX Station FIRE alarm (confirmed) |  |  | FACP | Modbus TCP / dry contacts | 10019 | On state = 1 | 1
FIRE.FZ_INV.FAULT | Fire Detection & Suppression | FZ_INV | FAULT | DI | Inverter / PV TX Station detection loop fault |  |  | FACP | Modbus TCP / dry contacts | 10020 | On state = 1 | 3
FIRE.FZ_INV.DISABLED | Fire Detection & Suppression | FZ_INV | DISABLED | DI | Inverter / PV TX Station zone disabled / isolated |  |  | FACP | Modbus TCP / dry contacts | 10021 | On state = 1 | 3
FIRE.FZ_DG.PRE_ALM | Fire Detection & Suppression | FZ_DG | PRE_ALM | DI | DG Enclosures pre-alarm (1st detector) |  |  | FACP | Modbus TCP / dry contacts | 10022 | On state = 1 | 2
FIRE.FZ_DG.FIRE | Fire Detection & Suppression | FZ_DG | FIRE | DI | DG Enclosures FIRE alarm (confirmed) |  |  | FACP | Modbus TCP / dry contacts | 10023 | On state = 1 | 1
FIRE.FZ_DG.FAULT | Fire Detection & Suppression | FZ_DG | FAULT | DI | DG Enclosures detection loop fault |  |  | FACP | Modbus TCP / dry contacts | 10024 | On state = 1 | 3
FIRE.FZ_DG.DISABLED | Fire Detection & Suppression | FZ_DG | DISABLED | DI | DG Enclosures zone disabled / isolated |  |  | FACP | Modbus TCP / dry contacts | 10025 | On state = 1 | 3
FIRE.FZ_CTRL.PRE_ALM | Fire Detection & Suppression | FZ_CTRL | PRE_ALM | DI | Control Room pre-alarm (1st detector) |  |  | FACP | Modbus TCP / dry contacts | 10026 | On state = 1 | 2
FIRE.FZ_CTRL.FIRE | Fire Detection & Suppression | FZ_CTRL | FIRE | DI | Control Room FIRE alarm (confirmed) |  |  | FACP | Modbus TCP / dry contacts | 10027 | On state = 1 | 1
FIRE.FZ_CTRL.FAULT | Fire Detection & Suppression | FZ_CTRL | FAULT | DI | Control Room detection loop fault |  |  | FACP | Modbus TCP / dry contacts | 10028 | On state = 1 | 3
FIRE.FZ_CTRL.DISABLED | Fire Detection & Suppression | FZ_CTRL | DISABLED | DI | Control Room zone disabled / isolated |  |  | FACP | Modbus TCP / dry contacts | 10029 | On state = 1 | 3
FIRE.FZ_CTRL.REL_PENDING | Fire Detection & Suppression | FZ_CTRL | REL_PENDING | DI | Control Room extinguishant release countdown |  |  | FACP | Modbus TCP / dry contacts | 10030 | On state = 1 | 1
FIRE.FZ_CTRL.RELEASED | Fire Detection & Suppression | FZ_CTRL | RELEASED | DI | Control Room extinguishant released |  |  | FACP | Modbus TCP / dry contacts | 10031 | On state = 1 | 1
FIRE.FZ_CTRL.MAN_INHIBIT | Fire Detection & Suppression | FZ_CTRL | MAN_INHIBIT | DI | Control Room manual / auto inhibit selected |  |  | FACP | Modbus TCP / dry contacts | 10032 | On state = 1 | 3
FIRE.FZ_CTRL.CYL_LOW | Fire Detection & Suppression | FZ_CTRL | CYL_LOW | DI | Control Room agent cylinder pressure low |  |  | FACP | Modbus TCP / dry contacts | 10033 | On state = 1 | 2
FIRE.FACP.HEALTHY | Fire Detection & Suppression | FACP | HEALTHY | DI | Fire alarm control panel healthy |  |  | FACP | Modbus TCP / dry contacts | 10034 | On state = 0 | 2
FIRE.FACP.SOUNDERS | Fire Detection & Suppression | FACP | SOUNDERS | DI | Sounders / beacons active |  |  | FACP | Modbus TCP / dry contacts | 10035
FIRE.FACP.CMD_SILENCE | Fire Detection & Suppression | FACP | CMD_SILENCE | DO | Silence sounders (remote) |  |  | FACP | Modbus TCP / dry contacts | 1
FIRE.FACP.CMD_RESET | Fire Detection & Suppression | FACP | CMD_RESET | DO | Fire panel reset (remote) |  |  | FACP | Modbus TCP / dry contacts | 2
AUX.UPS_SCADA.ON_BATT | UPS & Auxiliary Power | UPS_SCADA | ON_BATT | DI | SCADA / Comms UPS on battery |  |  | UPS_SCADA | SNMP v3 |  | On state = 1 | 3
AUX.UPS_SCADA.BYPASS | UPS & Auxiliary Power | UPS_SCADA | BYPASS | DI | SCADA / Comms UPS on bypass |  |  | UPS_SCADA | SNMP v3 |  | On state = 1 | 3
AUX.UPS_SCADA.FAULT | UPS & Auxiliary Power | UPS_SCADA | FAULT | DI | SCADA / Comms UPS fault |  |  | UPS_SCADA | SNMP v3 |  | On state = 1 | 2
AUX.UPS_SCADA.BATT_LOW | UPS & Auxiliary Power | UPS_SCADA | BATT_LOW | DI | SCADA / Comms UPS battery low |  |  | UPS_SCADA | SNMP v3 |  | On state = 1 | 2
AUX.UPS_SCADA.LOAD | UPS & Auxiliary Power | UPS_SCADA | LOAD | AI | SCADA / Comms UPS load | % |  | UPS_SCADA | SNMP v3 |  | Limits | 1/2 |  |  | 80 | 95
AUX.UPS_SCADA.AUTONOMY | UPS & Auxiliary Power | UPS_SCADA | AUTONOMY | AI | SCADA / Comms UPS battery autonomy | min |  | UPS_SCADA | SNMP v3 |  | Limits | 1/2 | 10 | 30
AUX.UPS_SCADA.U_OUT | UPS & Auxiliary Power | UPS_SCADA | U_OUT | AI | SCADA / Comms UPS output voltage | V |  | UPS_SCADA | SNMP v3
AUX.UPS_RMUP.ON_BATT | UPS & Auxiliary Power | UPS_RMUP | ON_BATT | DI | President RMU UPS on battery |  |  | UPS_RMUP | Dry contacts via RMU relay |  | On state = 1 | 3
AUX.UPS_RMUP.BYPASS | UPS & Auxiliary Power | UPS_RMUP | BYPASS | DI | President RMU UPS on bypass |  |  | UPS_RMUP | Dry contacts via RMU relay |  | On state = 1 | 3
AUX.UPS_RMUP.FAULT | UPS & Auxiliary Power | UPS_RMUP | FAULT | DI | President RMU UPS fault |  |  | UPS_RMUP | Dry contacts via RMU relay |  | On state = 1 | 2
AUX.UPS_RMUP.BATT_LOW | UPS & Auxiliary Power | UPS_RMUP | BATT_LOW | DI | President RMU UPS battery low |  |  | UPS_RMUP | Dry contacts via RMU relay |  | On state = 1 | 2
AUX.UPS_RMUM.ON_BATT | UPS & Auxiliary Power | UPS_RMUM | ON_BATT | DI | P.M. RMU UPS on battery |  |  | UPS_RMUM | Dry contacts via RMU relay |  | On state = 1 | 3
AUX.UPS_RMUM.BYPASS | UPS & Auxiliary Power | UPS_RMUM | BYPASS | DI | P.M. RMU UPS on bypass |  |  | UPS_RMUM | Dry contacts via RMU relay |  | On state = 1 | 3
AUX.UPS_RMUM.FAULT | UPS & Auxiliary Power | UPS_RMUM | FAULT | DI | P.M. RMU UPS fault |  |  | UPS_RMUM | Dry contacts via RMU relay |  | On state = 1 | 2
AUX.UPS_RMUM.BATT_LOW | UPS & Auxiliary Power | UPS_RMUM | BATT_LOW | DI | P.M. RMU UPS battery low |  |  | UPS_RMUM | Dry contacts via RMU relay |  | On state = 1 | 2
NET.N01.OK | Communications & Cybersecurity | N01 | OK | DI | RTU / SCADA Server A online |  | RTU / SCADA Server A | SCADA | ICMP / SNMP v3 |  | On state = 0 | 1
NET.N02.OK | Communications & Cybersecurity | N02 | OK | DI | SCADA Server B (hot standby) online |  | SCADA Server B (hot standby) | SCADA | ICMP / SNMP v3 |  | On state = 0 | 1
NET.N03.OK | Communications & Cybersecurity | N03 | OK | DI | Historian online |  | Historian | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N04.OK | Communications & Cybersecurity | N04 | OK | DI | HMI Workstation 1 online |  | HMI Workstation 1 | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N05.OK | Communications & Cybersecurity | N05 | OK | DI | HMI Workstation 2 online |  | HMI Workstation 2 | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N06.OK | Communications & Cybersecurity | N06 | OK | DI | Engineering Workstation online |  | Engineering Workstation | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N07.OK | Communications & Cybersecurity | N07 | OK | DI | PPC Controller online |  | PPC Controller | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N08.OK | Communications & Cybersecurity | N08 | OK | DI | blue'Log XM 5000 (weather station) online |  | blue'Log XM 5000 (weather station) | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N09.OK | Communications & Cybersecurity | N09 | OK | DI | Firewall / VPN gateway online |  | Firewall / VPN gateway | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N10.OK | Communications & Cybersecurity | N10 | OK | DI | Core switch A online |  | Core switch A | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N11.OK | Communications & Cybersecurity | N11 | OK | DI | Core switch B online |  | Core switch B | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N12.OK | Communications & Cybersecurity | N12 | OK | DI | GPS time server online |  | GPS time server | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N13.OK | Communications & Cybersecurity | N13 | OK | DI | Inverter PLC box online |  | Inverter PLC box | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N14.OK | Communications & Cybersecurity | N14 | OK | DI | BESS EMS online |  | BESS EMS | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N15.OK | Communications & Cybersecurity | N15 | OK | DI | DG controller network online |  | DG controller network | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N16.OK | Communications & Cybersecurity | N16 | OK | DI | Fibre ring - President RMU online |  | Fibre ring - President RMU | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.N17.OK | Communications & Cybersecurity | N17 | OK | DI | Fibre ring - P.M. RMU online |  | Fibre ring - P.M. RMU | SCADA | ICMP / SNMP v3 |  | On state = 0 | 2
NET.SEC.LOGIN_FAIL | Communications & Cybersecurity | SEC | LOGIN_FAIL | DI | Repeated failed log-in attempts (security) |  |  | SCADA | Syslog |  | On state = 1 | 2
NET.SEC.FW_DENY | Communications & Cybersecurity | SEC | FW_DENY | AI | Firewall denied connections (last hour) |  |  | FW | Syslog |  | Limits | 1/2 |  |  | 50
NET.SEC.TIME_SYNC | Communications & Cybersecurity | SEC | TIME_SYNC | DI | Time synchronisation (NTP/PTP) locked |  |  | GPS | NTP |  | On state = 0 | 3
PPC.PLANT.P_LOAD | Power Plant Controller | PLANT | P_LOAD | AI | Total plant load | kW |  | PPC | Internal
PPC.PLANT.P_PV | Power Plant Controller | PLANT | P_PV | AI | Total PV generation | kW |  | PPC | Internal
PPC.PLANT.P_PV_AVAIL | Power Plant Controller | PLANT | P_PV_AVAIL | AI | Available PV power | kW |  | PPC | Internal
PPC.PLANT.P_DG | Power Plant Controller | PLANT | P_DG | AI | Total DG generation | kW |  | PPC | Internal
PPC.PLANT.P_BESS | Power Plant Controller | PLANT | P_BESS | AI | BESS net power | kW |  | PPC | Internal
PPC.PLANT.RE_SHARE | Power Plant Controller | PLANT | RE_SHARE | AI | Renewable share (instant) | % |  | PPC | Internal
PPC.PLANT.E_LOAD_DAY | Power Plant Controller | PLANT | E_LOAD_DAY | AI | Load energy today | kWh |  | PPC | Internal
PPC.PLANT.E_PV_DAY | Power Plant Controller | PLANT | E_PV_DAY | AI | PV energy today | kWh |  | PPC | Internal
PPC.PLANT.E_DG_DAY | Power Plant Controller | PLANT | E_DG_DAY | AI | DG energy today | kWh |  | PPC | Internal
PPC.PLANT.FUEL_SAVED | Power Plant Controller | PLANT | FUEL_SAVED | AI | Diesel saved today | L |  | PPC | Internal
PPC.PLANT.CO2_SAVED | Power Plant Controller | PLANT | CO2_SAVED | AI | CO2 avoided today | t |  | PPC | Internal
PPC.PLANT.CURTAIL | Power Plant Controller | PLANT | CURTAIL | AI | PV curtailment | kW |  | PPC | Internal
PPC.CTRL.MODE | Power Plant Controller | CTRL | MODE | AO | PPC mode (0 manual, 1 auto) |  | 0-1 | PPC | Internal
PPC.CTRL.STATE | Power Plant Controller | CTRL | STATE | AI | PPC sequence state |  |  | PPC | Internal
PPC.CTRL.SP_SOC_DG_START | Power Plant Controller | CTRL | SP_SOC_DG_START | AO | SOC for DG start | % | 10-60 | PPC | Internal
PPC.CTRL.SP_SOC_DG_STOP | Power Plant Controller | CTRL | SP_SOC_DG_STOP | AO | SOC for DG stop | % | 40-95 | PPC | Internal
PPC.CTRL.SP_SOC_HIGH | Power Plant Controller | CTRL | SP_SOC_HIGH | AO | SOC for PV curtailment | % | 80-98 | PPC | Internal
PPC.CTRL.SP_DG_MINLOAD | Power Plant Controller | CTRL | SP_DG_MINLOAD | AO | DG minimum load | % | 20-50 | PPC | Internal
PPC.CTRL.SP_PF | Power Plant Controller | CTRL | SP_PF | AO | Plant power factor target |  | 0.85-1 | PPC | Internal
PPC.CTRL.ESD | Power Plant Controller | CTRL | ESD | DI | Plant emergency shutdown active |  |  | PPC | Internal |  | On state = 1 | 1
PPC.CTRL.LOAD_SHED | Power Plant Controller | CTRL | LOAD_SHED | DI | Load shedding active |  |  | PPC | Internal |  | On state = 1 | 2
PPC.CTRL.CMD_BLACKSTART | Power Plant Controller | CTRL | CMD_BLACKSTART | DO | Initiate black-start sequence |  |  | PPC | Internal
PPC.CTRL.CMD_ESD | Power Plant Controller | CTRL | CMD_ESD | DO | Plant emergency shutdown |  |  | PPC | Internal