## Read Me
Villa Somalia Hybrid Plant: SCADA Bill of Material
Project | Solarization of Villa Somalia, Mogadishu. 1,516 kWp PV, 3,340 kWh BESS, 2 diesel generators, 11 kV switchboard, 2 office transformer stations.
Basis | SICAM A8000 design: SCADA Design Report Rev 1, Device and I/O List Rev 1, drawing set BFE/PR/26/01-SCADA-001 to 005.
Status | Rev A, 22 Oct 2026, for pricing and supplier quotations. Quantities fixed by the design; prices to be entered.
Architecture | Two CP-8050 in hot standby; six I/O rows (24 modules, 244 hardwired signals, 27 % spare); SICAM SCC on two servers by IEC 60870-5-104; managed fibre ring of 7 switches; one firewall with VPN off by default; GPS time.
Sheets
BOM by Panel | Every item grouped by the panel or area it goes into, with tag, quantity and notes. Use it to build and check the panels.
Summary | The same items totalled per order line. Enter unit prices here, once; the BOM by Panel picks them up.
IO Check | I/O modules per row against the hardwired signals of the I/O list, with spare capacity.
By Others | Equipment that the SCADA connects to but does not supply, and what the SCADA needs from each supplier.
Services | Engineering and site services, for the offer. Not materials.
Number status key
Checked | Ordering number found on a supplier listing or a Siemens configuration document.
From memory - confirm | Ordering code from knowledge of the maker's catalogue; not checked online. Confirm with the distributor.
To confirm with supplier | Product exists but its number was not found, or it is configured or licensed by quotation. Take it from the supplier.
TBC | Size, make or length not fixed yet. Shaded yellow.
Assumptions and points to confirm
1 | Control voltage 110 V DC for the controllers and I/O rows (selects PS-8642, CI-8532, CI-8533, DI-8112). Confirm that 110 V DC exists at the office stations, the BESS yard and the generator area. If only 230 V AC is available there, either add a 230 V AC to 110 V DC supply per panel or change those rows to the 24 V variants (CI-8531, DI-8110) fed from the SITOP.
2 | Siemens to confirm: CI-8533 and DO-8221 ordering numbers, the hot standby function and licence, switchover time, and how the I/O rows connect to both controllers.
3 | Network ordering codes (Moxa, Fortinet, Meinberg) are from memory. Siemens SCALANCE equivalents may be offered instead; keep the same port counts.
4 | Field switches at the stations and yard use a 5 A SITOP instead of the 20 A unit of the Device List, which is oversized for one switch and one gateway.
5 | Two items not in the Device List Rev 1 are added: a 19-inch server rack with console for the control room, and a small enclosure for SW-MV.
6 | Cable and fibre lengths are left open until the cable route drawings are available.
7 | Currency and prices: enter in the Summary sheet. Totals calculate automatically.

## BOM by Panel
Bill of material by panel – SICAM A8000 design
Item | Tag / use | Description | Manufacturer | Model | Order no. | Number status | Qty | Unit | Unit price | Total price | Location | Notes | Group | Key
P1 | SCADA cabinet, 11 kV switchroom (controller pair, I/O rows 1 and 2, core network)
P1.01 | CP-8050 A, CP-8050 B | Processor module, SICAM A8000 | Siemens | CP-8050 | 6MF2805-0AA00 | Checked | 2 | pc |  |  | 11 kV switchroom | Hot standby pair: A active, B standby. | P1 | CP8050
P1.02 | Two per controller | Power supply 110-220 V DC, 45 W | Siemens | PS-8642 | 6MF2864-2AA00 | Checked | 4 | pc |  |  | 11 kV switchroom | Confirm the CP-8050 accepts a second supply. | P1 | PS8642
P1.03 | One per controller | Ethernet interface, 5 x RJ45 | Siemens | CI-8520 | 6MF2852-0AA00 | Checked | 2 | pc |  |  | 11 kV switchroom | Separate port per network zone; not a switch. | P1 | CI8520
P1.04 | One per controller | SICAM flash card, 2 GB | Siemens | SICAM flash card | 6MF1213-1GA05-0AA0 | Checked | 2 | pc |  |  | 11 kV switchroom |  | P1 | FLASH
P1.05 | One set per controller | Protocol licences for one CP-8050: IEC 60870-5-104 server, Modbus TCP client, IEC 61850 client, hot standby function | Siemens | CP-8050 licences | By quotation | To confirm with supplier | 2 | set |  |  | 11 kV switchroom | Including the hot standby function if licensed separately (open point 12). | P1 | LIC
P1.06 | Row 1 interface | I/O remote interface, electrical, 110-220 V DC | Siemens | CI-8532 | 6MF2853-2AA00 | Checked | 1 | pc |  |  | 11 kV switchroom | Row 1 on its own interface so both controllers reach it. | P1 | CI8532
P1.07 | R1-DI01 to R1-DI05 | Digital input, 2 x 8 inputs, 110 V DC | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 5 | pc |  |  | 11 kV switchroom | 11 kV panels AH1 to AH8. | P1 | DI8112
P1.08 | R1-CO01, R1-CO02 | Secured command output, 12 outputs, 1-out-of-n check | Siemens | DO-8221 | To confirm | To confirm with supplier | 2 | pc |  |  | 11 kV switchroom | Breaker open and close AH1 to AH7. | P1 | DO8221
P1.09 | R1-DO01 | Digital output, 8 relays, 24-220 V DC / 230 V AC | Siemens | DO-8212 | 6MF2821-2AA00 | Checked | 1 | pc |  |  | 11 kV switchroom | Alarm beacon, controller healthy. | P1 | DO8212
P1.10 | Row 2 interface | I/O remote interface, electrical, 110-220 V DC | Siemens | CI-8532 | 6MF2853-2AA00 | Checked | 1 | pc |  |  | 11 kV switchroom |  | P1 | CI8532
P1.11 | R2-DI01, R2-DI02 | Digital input, 2 x 8 inputs, 110 V DC | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 2 | pc |  |  | 11 kV switchroom | Auxiliary TX, LV board, UPS, DC, E-stop, doors. | P1 | DI8112
P1.12 | R2-AI01 | Analogue input, 4 x 4-20 mA | Siemens | AI-8320 | 6MF2832-0AA00 | Checked | 1 | pc |  |  | 11 kV switchroom | DC bus voltages. | P1 | AI8320
P1.13 | SW-CORE-A, SW-CORE-B | Managed core switch, 8 x RJ45 + 4 x gigabit SFP | Moxa | EDS-G512E | EDS-G512E-4GSFP | From memory - confirm | 2 | pc |  |  | 11 kV switchroom |  | P1 | CORE
P1.14 | Two per core switch | SFP transceiver, gigabit, single-mode, LC | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 4 | pc |  |  | 11 kV switchroom | Ring ports and the core A-B link. | P1 | SFP
P1.15 | FW-01 | Rugged firewall with VPN | Fortinet | FortiGate Rugged 60F | FGR-60F | From memory - confirm | 1 | pc |  |  | 11 kV switchroom | Second unit optional. | P1 | FW
P1.16 | GPS-01 | GPS time server with antenna, cable and surge protector | Meinberg | LANTIME M300 | M300/GPS | From memory - confirm | 1 | set |  |  | 11 kV switchroom | Antenna on the switchroom roof; cable length to suit. | P1 | GPS
P1.17 | Cabinet 24 V | 24 V DC power supply 20 A, input 85-275 V AC / 88-350 V DC | Siemens | SITOP PSU8200 24 V/20 A | 6EP1336-3BA10 | Checked | 1 | pc |  |  | 11 kV switchroom | Switches, firewall, gateway supply. Runs from the 110 V DC station battery. | P1 | PSU20
P1.18 | PM5560-AUX | Power meter with Ethernet, Modbus TCP | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | From memory - confirm | 1 | pc |  |  | 11 kV switchroom | Mounted in the auxiliary LV board. | P1 | PM5560
P1.19 | Fibre termination | Fibre patch panel, 24 x LC, rack or DIN | To suit | - | - | TBC | 1 | pc |  |  | 11 kV switchroom |  | P1 | FPP
P1.20 | SCADA cabinet | SCADA cabinet 800 x 2000 x 800 mm, with plinth | Rittal | VX25 | 8808.000 | From memory - confirm | 1 | pc |  |  | 11 kV switchroom | Door contact wired to row 2. | P1 | VX25
P1.21 | SCADA cabinet | Cabinet accessories: MCBs, terminals, surge protection, fans and thermostat, lighting, door switch, labels, wiring | To suit | - | - | TBC | 1 | lot |  |  | 11 kV switchroom |  | P1 | ACC_C
Subtotal P1
P2 | Control room (SCADA servers, operator and engineering stations)
P2.01 | SRV-A, SRV-B | SCADA server, rack industrial PC, redundant power supplies and disks | Siemens | SIMATIC IPC647E | Configured to order | To confirm with supplier | 2 | pc |  |  | Control room | Server A active, B hot standby. | P2 | IPC
P2.02 | Server rack | 19-inch rack 24U with rack console (monitor, keyboard, KVM) | To suit | - | - | TBC | 1 | set |  |  | Control room | Not in the Device List Rev 1; needed to house the rack servers and UPS. Confirm the room. | P2 | RACK
P2.03 | OWS-01 | Operator workstation | Dell | OptiPlex 7000 series | Configured to order | To confirm with supplier | 1 | pc |  |  | Control room |  | P2 | OWS
P2.04 | OWS-01 | Monitor 24-inch, full HD | Dell | P2425H or equal | To suit | To confirm with supplier | 2 | pc |  |  | Control room | Two monitors. | P2 | MON
P2.05 | ENG-01 | Engineering laptop, rugged | Dell | Latitude 5430 Rugged | Configured to order | To confirm with supplier | 1 | pc |  |  | Control room |  | P2 | LAP
P2.06 | UPS-01 | UPS 3000 VA online, rack, network card | APC | Smart-UPS SRT 3000 | SRT3000RMXLI | From memory - confirm | 1 | pc |  |  | Control room | SNMP to the SCADA. | P2 | UPS
P2.07 | UPS-01 | External battery pack for the UPS (about 2 h runtime, to size) | APC | SRT96RMBP | SRT96RMBP | From memory - confirm | 1 | pc |  |  | Control room | Size for the runtime the client requires. | P2 | UPSB
P2.08 | ALM-01 | Alarm sounder and beacon | Pfannenberg | PATROL | Model to suit | TBC | 1 | pc |  |  | Control room | Hardwired to row 1. | P2 | BEACON
Subtotal P2
P3 | President station I/O panel (row 3, SW-PRS)
P3.01 | Row 3 interface | I/O remote interface, optical, 110-220 V DC | Siemens | CI-8533 | To confirm | To confirm with supplier | 1 | pc |  |  | President office transformer station | Confirm fibre type and maximum length. | P3 | CI8533
P3.02 | R3-DI01 to R3-DI03 | Digital input, 2 x 8 inputs, 110 V DC | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 3 | pc |  |  | President office transformer station | RMU, 630 kVA transformer, LVDB. | P3 | DI8112
P3.03 | R3-CO01 | Secured command output, 12 outputs, 1-out-of-n check | Siemens | DO-8221 | To confirm | To confirm with supplier | 1 | pc |  |  | President office transformer station | RMU and LVDB commands. | P3 | DO8221
P3.04 | SW-PRS | Managed field switch, 7 x RJ45 + 3 x gigabit combo/SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | 1 | pc |  |  | President office transformer station |  | P3 | FSW
P3.05 | SW-PRS ring ports | SFP transceiver, gigabit, single-mode, LC | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 2 | pc |  |  | President office transformer station |  | P3 | SFP
P3.06 | MGate-PRS | Modbus RTU to Modbus TCP gateway, 1 port | Moxa | MGate MB3170 | MB3170 | From memory - confirm | 1 | pc |  |  | President office transformer station | ST260E RMU relay, RS485. | P3 | MGATE
P3.07 | Panel 24 V | 24 V DC power supply 5 A, input 85-264 V AC / 110-300 V DC | Siemens | SITOP PSU8200 24 V/5 A | 6EP1333-3BA10 | From memory - confirm | 1 | pc |  |  | President office transformer station | Smaller than the 20 A unit in the Device List, which is oversized here. | P3 | PSU5
P3.08 | PM5560-PRS | Power meter with Ethernet, Modbus TCP | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | From memory - confirm | 1 | pc |  |  | President office transformer station | Mounted in the LVDB. | P3 | PM5560
P3.09 | Fibre termination | Fibre splice box, DIN rail, 12 x LC | To suit | - | - | TBC | 1 | pc |  |  | President office transformer station |  | P3 | FSB
P3.10 | Row 3 panel | Outdoor I/O panel, IP55 minimum, with sun shade | Rittal | AX | Size to suit | TBC | 1 | pc |  |  | President office transformer station |  | P3 | AX
P3.11 | Row 3 panel | Panel accessories: MCBs, terminals, surge protection, anti-condensation heater and thermostat, door switch, labels, wiring | To suit | - | - | TBC | 1 | lot |  |  | President office transformer station |  | P3 | ACC_P
Subtotal P3
P4 | Prime Minister station I/O panel (row 4, SW-PMS)
P4.01 | Row 4 interface | I/O remote interface, optical, 110-220 V DC | Siemens | CI-8533 | To confirm | To confirm with supplier | 1 | pc |  |  | Prime Minister office transformer station | Confirm fibre type and maximum length. | P4 | CI8533
P4.02 | R4-DI01 to R4-DI03 | Digital input, 2 x 8 inputs, 110 V DC | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 3 | pc |  |  | Prime Minister office transformer station | RMU, 630 kVA transformer, LVDB. | P4 | DI8112
P4.03 | R4-CO01 | Secured command output, 12 outputs, 1-out-of-n check | Siemens | DO-8221 | To confirm | To confirm with supplier | 1 | pc |  |  | Prime Minister office transformer station | RMU and LVDB commands. | P4 | DO8221
P4.04 | SW-PMS | Managed field switch, 7 x RJ45 + 3 x gigabit combo/SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | 1 | pc |  |  | Prime Minister office transformer station |  | P4 | FSW
P4.05 | SW-PMS ring ports | SFP transceiver, gigabit, single-mode, LC | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 2 | pc |  |  | Prime Minister office transformer station |  | P4 | SFP
P4.06 | MGate-PMS | Modbus RTU to Modbus TCP gateway, 1 port | Moxa | MGate MB3170 | MB3170 | From memory - confirm | 1 | pc |  |  | Prime Minister office transformer station | ST260E RMU relay, RS485. | P4 | MGATE
P4.07 | Panel 24 V | 24 V DC power supply 5 A, input 85-264 V AC / 110-300 V DC | Siemens | SITOP PSU8200 24 V/5 A | 6EP1333-3BA10 | From memory - confirm | 1 | pc |  |  | Prime Minister office transformer station |  | P4 | PSU5
P4.08 | PM5560-PMS | Power meter with Ethernet, Modbus TCP | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | From memory - confirm | 1 | pc |  |  | Prime Minister office transformer station | Mounted in the LVDB. | P4 | PM5560
P4.09 | Fibre termination | Fibre splice box, DIN rail, 12 x LC | To suit | - | - | TBC | 1 | pc |  |  | Prime Minister office transformer station |  | P4 | FSB
P4.10 | Row 4 panel | Outdoor I/O panel, IP55 minimum, with sun shade | Rittal | AX | Size to suit | TBC | 1 | pc |  |  | Prime Minister office transformer station |  | P4 | AX
P4.11 | Row 4 panel | Panel accessories: MCBs, terminals, surge protection, anti-condensation heater and thermostat, door switch, labels, wiring | To suit | - | - | TBC | 1 | lot |  |  | Prime Minister office transformer station |  | P4 | ACC_P
Subtotal P4
P5 | BESS and inverter transformer yard I/O panel (row 5, SW-BESS)
P5.01 | Row 5 interface | I/O remote interface, optical, 110-220 V DC | Siemens | CI-8533 | To confirm | To confirm with supplier | 1 | pc |  |  | BESS yard |  | P5 | CI8533
P5.02 | R5-DI01, R5-DI02 | Digital input, 2 x 8 inputs, 110 V DC | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 2 | pc |  |  | BESS yard | Fire panel, BESS ACB, PV ACB, MCCBs, inverter TX. Spare 19 %: see I/O Check. | P5 | DI8112
P5.03 | SW-BESS | Managed field switch, 7 x RJ45 + 3 x gigabit combo/SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | 1 | pc |  |  | BESS yard | Mounted in the row 5 panel; Ethernet to the EMS in the container. | P5 | FSW
P5.04 | SW-BESS ring ports | SFP transceiver, gigabit, single-mode, LC | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 2 | pc |  |  | BESS yard |  | P5 | SFP
P5.05 | Panel 24 V | 24 V DC power supply 5 A, input 85-264 V AC / 110-300 V DC | Siemens | SITOP PSU8200 24 V/5 A | 6EP1333-3BA10 | From memory - confirm | 1 | pc |  |  | BESS yard |  | P5 | PSU5
P5.06 | Fibre termination | Fibre splice box, DIN rail, 12 x LC | To suit | - | - | TBC | 1 | pc |  |  | BESS yard |  | P5 | FSB
P5.07 | Row 5 panel | Outdoor I/O panel, IP55 minimum, with sun shade | Rittal | AX | Size to suit | TBC | 1 | pc |  |  | BESS yard |  | P5 | AX
P5.08 | Row 5 panel | Panel accessories: MCBs, terminals, surge protection, anti-condensation heater and thermostat, door switch, labels, wiring | To suit | - | - | TBC | 1 | lot |  |  | BESS yard |  | P5 | ACC_P
Subtotal P5
P6 | Generator area I/O panel (row 6, SW-GEN)
P6.01 | Row 6 interface | I/O remote interface, optical, 110-220 V DC | Siemens | CI-8533 | To confirm | To confirm with supplier | 1 | pc |  |  | Generator area |  | P6 | CI8533
P6.02 | R6-DI01, R6-DI02 | Digital input, 2 x 8 inputs, 110 V DC | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 2 | pc |  |  | Generator area | DG1, DG2, step-up TX, LV ACB. | P6 | DI8112
P6.03 | R6-AI01 | Analogue input, 4 x 4-20 mA | Siemens | AI-8320 | 6MF2832-0AA00 | Checked | 1 | pc |  |  | Generator area | Fuel level DG1, DG2. | P6 | AI8320
P6.04 | SW-GEN | Managed field switch, 7 x RJ45 + 3 x gigabit combo/SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | 1 | pc |  |  | Generator area |  | P6 | FSW
P6.05 | SW-GEN ring ports | SFP transceiver, gigabit, single-mode, LC | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 2 | pc |  |  | Generator area |  | P6 | SFP
P6.06 | Panel 24 V | 24 V DC power supply 5 A, input 85-264 V AC / 110-300 V DC | Siemens | SITOP PSU8200 24 V/5 A | 6EP1333-3BA10 | From memory - confirm | 1 | pc |  |  | Generator area |  | P6 | PSU5
P6.07 | MGate-GEN (option) | Modbus RTU to Modbus TCP gateway, 1 port | Moxa | MGate MB3170 | MB3170 | From memory - confirm | 0 | pc |  |  | Generator area | Only if the generator controllers are RS485 only (open point 3). Quantity 0 until confirmed. | P6 | MGATE
P6.08 | Fibre termination | Fibre splice box, DIN rail, 12 x LC | To suit | - | - | TBC | 1 | pc |  |  | Generator area |  | P6 | FSB
P6.09 | Row 6 panel | Outdoor I/O panel, IP55 minimum, with sun shade | Rittal | AX | Size to suit | TBC | 1 | pc |  |  | Generator area |  | P6 | AX
P6.10 | Row 6 panel | Panel accessories: MCBs, terminals, surge protection, anti-condensation heater and thermostat, door switch, labels, wiring | To suit | - | - | TBC | 1 | lot |  |  | Generator area |  | P6 | ACC_P
Subtotal P6
P7 | Inverter MV station network enclosure (SW-MV)
P7.01 | SW-MV | Managed field switch, 7 x RJ45 + 3 x gigabit combo/SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | 1 | pc |  |  | Inverter MV station | PLC box and blue'Log XM. | P7 | FSW
P7.02 | SW-MV ring ports | SFP transceiver, gigabit, single-mode, LC | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 2 | pc |  |  | Inverter MV station |  | P7 | SFP
P7.03 | Enclosure 24 V | 24 V DC power supply 5 A, input 85-264 V AC / 110-300 V DC | Siemens | SITOP PSU8200 24 V/5 A | 6EP1333-3BA10 | From memory - confirm | 1 | pc |  |  | Inverter MV station |  | P7 | PSU5
P7.04 | Fibre termination | Fibre splice box, DIN rail, 12 x LC | To suit | - | - | TBC | 1 | pc |  |  | Inverter MV station |  | P7 | FSB
P7.05 | SW-MV enclosure | Small wall enclosure for field switch, IP55 | Rittal | AX | Size to suit | TBC | 1 | pc |  |  | Inverter MV station | Not in the Device List Rev 1. Omit if the switch fits in the PLC box cabinet. | P7 | AXS
P7.06 | SW-MV enclosure | Panel accessories: MCBs, terminals, surge protection, anti-condensation heater and thermostat, door switch, labels, wiring | To suit | - | - | TBC | 1 | lot |  |  | Inverter MV station |  | P7 | ACC_P
Subtotal P7
C | Cables and passive network material (site-wide; lengths from the cable route drawings)
C.01 | 3 routes | Single-mode OS2 fibre cable, 12 core, armoured, outdoor | To suit | - | - | TBC |  | m |  |  | Site | Switchroom-President, switchroom-PM, President-PM; yard and generator area on spare cores. Length per route TBC. | C | FIBRE
C.02 | All fibre panels | Fibre patch cord LC-LC single-mode duplex, 2 m | To suit | - | - | TBC | 20 | pc |  |  | Site |  | C | FCORD
C.03 | Control room, switchroom, stations | Cat6 S/FTP industrial cable | To suit | - | - | TBC |  | m |  |  | Site | Length TBC. Control room to switchroom assumed under 90 m; otherwise fibre. | C | CAT6
C.04 | All panels | Cat6 S/FTP patch cord, 1 to 3 m | To suit | - | - | TBC | 40 | pc |  |  | Site |  | C | PCORD
C.05 | Field connections | Shielded field RJ45 connector | To suit | - | - | TBC | 30 | pc |  |  | Site |  | C | RJ45
C.06 | MGate to ST260E | RS485 cable, 2-pair shielded twisted pair, 120 ohm | To suit | - | - | TBC |  | m |  |  | Site | Short runs inside the stations. Length TBC. | C | RS485
C.07 | Hardwired I/O | Control cable, multicore 1.0 mm2, screened, for hardwired I/O | To suit | - | - | TBC |  | m |  |  | Site | 244 hardwired signals. Length per cable schedule TBC. | C | CTRL
Subtotal C
S | Software and licences
S.01 | SRV-A, SRV-B | Substation SCADA, redundant server pair, about 1,000 data points, IEC 60870-5-104, two user roles | Siemens | SICAM SCC | By quotation | To confirm with supplier | 1 | lic |  |  | SCADA servers and stations | 707 signals today plus about 30 % growth. | S | SCC
S.02 | OWS-01 | SICAM SCC client licence for the operator workstation | Siemens | SICAM SCC client | By quotation | To confirm with supplier | 1 | lic |  |  | SCADA servers and stations | Confirm whether the operator station runs as a client or as a web client. | S | SCCC
S.03 | ENG-01 | Controller engineering tool | Siemens | SICAM Device Manager | By quotation | To confirm with supplier | 1 | lic |  |  | SCADA servers and stations |  | S | DM
S.04 | SRV-A, SRV-B | Server operating system | Microsoft | Windows Server Standard | OEM with the IPC | To confirm with supplier | 2 | lic |  |  | SCADA servers and stations | Usually supplied with the IPC. | S | WINS
S.05 | SRV-A | Network management, at least 16 nodes | Moxa | MXview One | By quotation | To confirm with supplier | 1 | lic |  |  | SCADA servers and stations | Covers 7 switches, firewall, gateways, meters, UPS. | S | NMS
S.06 | FW-01 | Firewall security services and support, 3 years | Fortinet | FortiGate Rugged 60F bundle | By quotation | To confirm with supplier | 1 | lic |  |  | SCADA servers and stations | VPN client (FortiClient) is free. | S | FWLIC
Subtotal S
SP | Recommended spare parts (commissioning and first two years)
SP.01 | Spare | Digital input, 2 x 8 inputs, 110 V DC | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 1 | pc |  |  | Store |  | SP | DI8112
SP.02 | Spare | Secured command output, 12 outputs, 1-out-of-n check | Siemens | DO-8221 | To confirm | To confirm with supplier | 1 | pc |  |  | Store |  | SP | DO8221
SP.03 | Spare | I/O remote interface, optical, 110-220 V DC | Siemens | CI-8533 | To confirm | To confirm with supplier | 1 | pc |  |  | Store |  | SP | CI8533
SP.04 | Spare | Power supply 110-220 V DC, 45 W | Siemens | PS-8642 | 6MF2864-2AA00 | Checked | 1 | pc |  |  | Store |  | SP | PS8642
SP.05 | Spare | SICAM flash card, 2 GB | Siemens | SICAM flash card | 6MF1213-1GA05-0AA0 | Checked | 1 | pc |  |  | Store | Keep a copy of the controller configuration on it. | SP | FLASH
SP.06 | Spare | Managed field switch, 7 x RJ45 + 3 x gigabit combo/SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | 1 | pc |  |  | Store |  | SP | FSW
SP.07 | Spare | SFP transceiver, gigabit, single-mode, LC | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 2 | pc |  |  | Store |  | SP | SFP
SP.08 | Spare | 24 V DC power supply 5 A, input 85-264 V AC / 110-300 V DC | Siemens | SITOP PSU8200 24 V/5 A | 6EP1333-3BA10 | From memory - confirm | 1 | pc |  |  | Store |  | SP | PSU5
SP.09 | Spare | Modbus RTU to Modbus TCP gateway, 1 port | Moxa | MGate MB3170 | MB3170 | From memory - confirm | 1 | pc |  |  | Store |  | SP | MGATE
Subtotal SP
Total materials

## Summary
Summary by order line | [6 empty] | Currency: | [USD]
Line | Description | Manufacturer | Model | Order no. | Number status | Unit | Total qty | Unit price | Total price | Used in | Key
1 | Processor module, SICAM A8000 | Siemens | CP-8050 | 6MF2805-0AA00 | Checked | pc |  |  |  | P1 | CP8050
2 | Power supply 110-220 V DC, 45 W | Siemens | PS-8642 | 6MF2864-2AA00 | Checked | pc |  |  |  | P1, SP | PS8642
3 | Ethernet interface, 5 x RJ45 | Siemens | CI-8520 | 6MF2852-0AA00 | Checked | pc |  |  |  | P1 | CI8520
4 | SICAM flash card, 2 GB | Siemens | SICAM flash card | 6MF1213-1GA05-0AA0 | Checked | pc |  |  |  | P1, SP | FLASH
5 | Protocol licences for one CP-8050: IEC 60870-5-104 server, Modbus TCP client, IEC 61850 client, hot standby function | Siemens | CP-8050 licences | By quotation | To confirm with supplier | set |  |  |  | P1 | LIC
6 | I/O remote interface, electrical, 110-220 V DC | Siemens | CI-8532 | 6MF2853-2AA00 | Checked | pc |  |  |  | P1 | CI8532
7 | Digital input, 2 x 8 inputs, 110 V DC | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | pc |  |  |  | P1, P3, P4, P5, P6, SP | DI8112
8 | Secured command output, 12 outputs, 1-out-of-n check | Siemens | DO-8221 | To confirm | To confirm with supplier | pc |  |  |  | P1, P3, P4, SP | DO8221
9 | Digital output, 8 relays, 24-220 V DC / 230 V AC | Siemens | DO-8212 | 6MF2821-2AA00 | Checked | pc |  |  |  | P1 | DO8212
10 | Analogue input, 4 x 4-20 mA | Siemens | AI-8320 | 6MF2832-0AA00 | Checked | pc |  |  |  | P1, P6 | AI8320
11 | Managed core switch, 8 x RJ45 + 4 x gigabit SFP | Moxa | EDS-G512E | EDS-G512E-4GSFP | From memory - confirm | pc |  |  |  | P1 | CORE
12 | SFP transceiver, gigabit, single-mode, LC | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | pc |  |  |  | P1, P3, P4, P5, P6, P7, SP | SFP
13 | Rugged firewall with VPN | Fortinet | FortiGate Rugged 60F | FGR-60F | From memory - confirm | pc |  |  |  | P1 | FW
14 | GPS time server with antenna, cable and surge protector | Meinberg | LANTIME M300 | M300/GPS | From memory - confirm | set |  |  |  | P1 | GPS
15 | 24 V DC power supply 20 A, input 85-275 V AC / 88-350 V DC | Siemens | SITOP PSU8200 24 V/20 A | 6EP1336-3BA10 | Checked | pc |  |  |  | P1 | PSU20
16 | Power meter with Ethernet, Modbus TCP | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | From memory - confirm | pc |  |  |  | P1, P3, P4 | PM5560
17 | Fibre patch panel, 24 x LC, rack or DIN | To suit | - | - | TBC | pc |  |  |  | P1 | FPP
18 | SCADA cabinet 800 x 2000 x 800 mm, with plinth | Rittal | VX25 | 8808.000 | From memory - confirm | pc |  |  |  | P1 | VX25
19 | Cabinet accessories: MCBs, terminals, surge protection, fans and thermostat, lighting, door switch, labels, wiring | To suit | - | - | TBC | lot |  |  |  | P1 | ACC_C
20 | SCADA server, rack industrial PC, redundant power supplies and disks | Siemens | SIMATIC IPC647E | Configured to order | To confirm with supplier | pc |  |  |  | P2 | IPC
21 | 19-inch rack 24U with rack console (monitor, keyboard, KVM) | To suit | - | - | TBC | set |  |  |  | P2 | RACK
22 | Operator workstation | Dell | OptiPlex 7000 series | Configured to order | To confirm with supplier | pc |  |  |  | P2 | OWS
23 | Monitor 24-inch, full HD | Dell | P2425H or equal | To suit | To confirm with supplier | pc |  |  |  | P2 | MON
24 | Engineering laptop, rugged | Dell | Latitude 5430 Rugged | Configured to order | To confirm with supplier | pc |  |  |  | P2 | LAP
25 | UPS 3000 VA online, rack, network card | APC | Smart-UPS SRT 3000 | SRT3000RMXLI | From memory - confirm | pc |  |  |  | P2 | UPS
26 | External battery pack for the UPS (about 2 h runtime, to size) | APC | SRT96RMBP | SRT96RMBP | From memory - confirm | pc |  |  |  | P2 | UPSB
27 | Alarm sounder and beacon | Pfannenberg | PATROL | Model to suit | TBC | pc |  |  |  | P2 | BEACON
28 | I/O remote interface, optical, 110-220 V DC | Siemens | CI-8533 | To confirm | To confirm with supplier | pc |  |  |  | P3, P4, P5, P6, SP | CI8533
29 | Managed field switch, 7 x RJ45 + 3 x gigabit combo/SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | pc |  |  |  | P3, P4, P5, P6, P7, SP | FSW
30 | Modbus RTU to Modbus TCP gateway, 1 port | Moxa | MGate MB3170 | MB3170 | From memory - confirm | pc |  |  |  | P3, P4, P6, SP | MGATE
31 | 24 V DC power supply 5 A, input 85-264 V AC / 110-300 V DC | Siemens | SITOP PSU8200 24 V/5 A | 6EP1333-3BA10 | From memory - confirm | pc |  |  |  | P3, P4, P5, P6, P7, SP | PSU5
32 | Fibre splice box, DIN rail, 12 x LC | To suit | - | - | TBC | pc |  |  |  | P3, P4, P5, P6, P7 | FSB
33 | Outdoor I/O panel, IP55 minimum, with sun shade | Rittal | AX | Size to suit | TBC | pc |  |  |  | P3, P4, P5, P6 | AX
34 | Panel accessories: MCBs, terminals, surge protection, anti-condensation heater and thermostat, door switch, labels, wiring | To suit | - | - | TBC | lot |  |  |  | P3, P4, P5, P6, P7 | ACC_P
35 | Small wall enclosure for field switch, IP55 | Rittal | AX | Size to suit | TBC | pc |  |  |  | P7 | AXS
36 | Single-mode OS2 fibre cable, 12 core, armoured, outdoor | To suit | - | - | TBC | m |  |  |  | C | FIBRE
37 | Fibre patch cord LC-LC single-mode duplex, 2 m | To suit | - | - | TBC | pc |  |  |  | C | FCORD
38 | Cat6 S/FTP industrial cable | To suit | - | - | TBC | m |  |  |  | C | CAT6
39 | Cat6 S/FTP patch cord, 1 to 3 m | To suit | - | - | TBC | pc |  |  |  | C | PCORD
40 | Shielded field RJ45 connector | To suit | - | - | TBC | pc |  |  |  | C | RJ45
41 | RS485 cable, 2-pair shielded twisted pair, 120 ohm | To suit | - | - | TBC | m |  |  |  | C | RS485
42 | Control cable, multicore 1.0 mm2, screened, for hardwired I/O | To suit | - | - | TBC | m |  |  |  | C | CTRL
43 | Substation SCADA, redundant server pair, about 1,000 data points, IEC 60870-5-104, two user roles | Siemens | SICAM SCC | By quotation | To confirm with supplier | lic |  |  |  | S | SCC
44 | SICAM SCC client licence for the operator workstation | Siemens | SICAM SCC client | By quotation | To confirm with supplier | lic |  |  |  | S | SCCC
45 | Controller engineering tool | Siemens | SICAM Device Manager | By quotation | To confirm with supplier | lic |  |  |  | S | DM
46 | Server operating system | Microsoft | Windows Server Standard | OEM with the IPC | To confirm with supplier | lic |  |  |  | S | WINS
47 | Network management, at least 16 nodes | Moxa | MXview One | By quotation | To confirm with supplier | lic |  |  |  | S | NMS
48 | Firewall security services and support, 3 years | Fortinet | FortiGate Rugged 60F bundle | By quotation | To confirm with supplier | lic |  |  |  | S | FWLIC
Total materials

## IO Check
I/O modules against the hardwired signals of the I/O list Rev 1
Row | Location | Interface | Modules | Module count | Channels | Signals used | Spare | Spare % | Remark
1 | 11 kV switchroom | CI-8532 | DI-8112 x5, DO-8221 x2, DO-8212 x1 | 8 | 112 | 87
2 | SCADA cabinet | CI-8532 | DI-8112 x2, AI-8320 x1 | 3 | 36 | 25
3 | President station | CI-8533 | DI-8112 x3, DO-8221 x1 | 4 | 60 | 43
4 | PM station | CI-8533 | DI-8112 x3, DO-8221 x1 | 4 | 60 | 43
5 | BESS / inverter yard | CI-8533 | DI-8112 x2 | 2 | 32 | 26 |  |  | Below the 20 % target: add a third DI-8112 if more yard signals appear.
6 | Generator area | CI-8533 | DI-8112 x2, AI-8320 x1 | 3 | 36 | 20
Total
| Check |  | I/O modules in the BOM (rows 1 to 6, without spares)

## By Others
Equipment the SCADA connects to but does not supply
No. | Equipment | Make / model | Supplied by | What the SCADA needs from the supplier
1 | PV string inverters NB01 to NB04 | Sungrow SG350HX | PV supplier | Power line communication to the PLC box; nothing connects to the SCADA directly.
2 | Power line communication box (PLC box) | Sungrow, model TBC | PV supplier | Ethernet port and Modbus TCP register map; written list of settings the SCADA may write.
3 | Embedded energy management system (EMS) | TBC | BESS / EMS supplier | Ethernet port, Modbus TCP point table, heartbeat, written list of settings the SCADA may write.
4 | Battery system 3,340 kWh | Sungrow ST3340UX | BESS supplier | Read through the EMS. Fire, E-stop and door volt-free contacts at a terminal strip.
5 | Generator controllers DG1, DG2 | TBC | Generator supplier | Modbus TCP (or RTU, then add MGate-GEN); volt-free contacts for GCB, running, alarm, E-stop; 4-20 mA fuel level.
6 | 11 kV protection relays AH1 to AH7 | TBC | Switchgear supplier | Ethernet, two ports preferred; IEC 61850 or Modbus TCP documentation. Motorised breakers and auxiliary contacts.
7 | Neutral earthing resistor panel AH8 | TBC | Switchgear supplier | Auxiliary contacts: breaker, earth switch, gas, earth fault.
8 | RMU protection relays | ST260E | RMU supplier | RS485 port and Modbus map; motorised switches.
9 | Transformers (inverter, DG step-up, auxiliary, 2 x 630 kVA) | TBC | Transformer supplier | Alarm and trip contacts wired to a terminal box.
10 | LV distribution boards and main breakers | TBC | Switchboard supplier | Space and CT for the PM5560 meters; breaker auxiliary contacts; motorised LVDB incomers.
11 | Fire detection and suppression panel | TBC | Fire system supplier | Volt-free contacts per the I/O list; direct trip of the battery outside the SCADA.
12 | UPS and 110 V DC station supplies | TBC | Electrical contractor | 110 V DC for the controllers and I/O rows; alarm contacts; Modbus TCP or SNMP.
13 | Weather station: blue'Log XM, SMP12-A, WindSonic, temperature sensors | Meteocontrol and others | PV supplier | Ethernet port and Modbus TCP documentation.
14 | RMU UPS 2 kVA | TBC | RMU supplier | On battery and fault contacts.

## Services
Engineering and services (for the offer; not materials)
No. | Service | Unit | Qty | Price
1 | Engineering: controller configuration, interlocks, IP plan, SCADA database and screens | lot | 1
2 | Panel build: SCADA cabinet and six field panels, with wiring and internal tests | lot | 1
3 | Factory acceptance test with the client | lot | 1
4 | Site installation supervision, termination and fibre splicing | lot | 1
5 | Site acceptance and interface tests with the PV, BESS, generator and switchgear suppliers | lot | 1
6 | Training: operators and administrators | lot | 1
7 | Documentation: as-built drawings, manuals, configuration backups | lot | 1
8 | Warranty and remote support, 2 years | lot | 1
Total services