## Read Me
Villa Somalia SCADA: corrected I/O allocation for the Schneider Electric requote
Item | Description
Purpose | Basis for Schneider Electric to requote the PLC and remote I/O. Allocates each hardwired signal of the Device and I/O List Rev 1 to a Schneider module and channel at the location where it is wired, and states the changes against the offer.
Offer reviewed | Offer Proposal Villa Somalia, version 1, 16 Oct 2026 (Schneider Electric), and its Bill of Material workbook.
Signal basis | Villa_Somalia_SCADA_Device_and_IO_List_Rev1.xlsx, sheet IO List: 244 hardwired signals (208 DI, 32 DO, 4 AI). The 463 communication points (sheet Comms Point List) are read over the network and need no I/O channels.
Why the offer does not fit | The offer has enough channels in total (416 DI, 192 DO) but they are in the wrong places: four PV inverter islands where the yard needs 26 inputs, no I/O in the generator area, no analogue inputs, both office islands labelled PM office, six times the outputs required, and no interposing relays for the breaker commands.
Locations | Switchroom (I/O rows 1 and 2 of the design), President station (row 3), Prime Minister station (row 4), BESS and inverter yard (row 5), generator area (row 6).
Switchroom I/O | All switchroom I/O sits in the Ethernet remote drop, none in the CPU rack, so the CPU rack can become a hot standby pair without rewiring (sheet Other Items, item 1).
Spare capacity | About 20 % or more spare digital inputs per location, as in the design: 27 % in the switchroom and office stations, 44 % in the generator area, 19 % in the BESS yard (add a third input module there if more yard signals appear). Outputs and analogue inputs are single modules with 50 % spare.
Inputs | Switchgear, RMU, transformer and package contacts are assumed dry contacts, wetted at 24 V DC from a field supply in each panel. Contacts that carry 110 V DC need an interposing relay; confirm with the terminal schedules.
Outputs | Breaker and switch commands drive interposing relays (32 in total: 30 commands, beacon and watchdog). The relay contact switches the 110 V DC control circuit; the 24 V DC transistor outputs never switch a coil directly.
Sheets | Hardware by Location: modules per location with used and spare channels, calculated. IO Allocation: every signal with its Schneider module and channel. Changes to Offer: line-by-line quantities. Other Items: what else must be quoted or clarified.
Status | Rev 0, 16 Oct 2026, for Schneider Electric to requote. Module and channel numbers are proposals; Schneider may re-number within a location if the totals and spare stay the same.

## Hardware by Location
I/O hardware by location
Used channels are counted from sheet IO Allocation.
Location | Design rows | Module | Module reference | Description | Channels | Used | Spare | Spare %
11 kV switchroom, M580 Ethernet remote drop (BMECRA31210 on BMEXBP1200) | 1, 2 | SWR-DI1 | BMXDDI3202K | X80 digital input, 32 channels, 24 V DC | 32
11 kV switchroom, M580 Ethernet remote drop (BMECRA31210 on BMEXBP1200) | 1, 2 | SWR-DI2 | BMXDDI3202K | X80 digital input, 32 channels, 24 V DC | 32
11 kV switchroom, M580 Ethernet remote drop (BMECRA31210 on BMEXBP1200) | 1, 2 | SWR-DI3 | BMXDDI3202K | X80 digital input, 32 channels, 24 V DC | 32
11 kV switchroom, M580 Ethernet remote drop (BMECRA31210 on BMEXBP1200) | 1, 2 | SWR-DI4 | BMXDDI3202K | X80 digital input, 32 channels, 24 V DC | 32
11 kV switchroom, M580 Ethernet remote drop (BMECRA31210 on BMEXBP1200) | 1, 2 | SWR-DO1 | BMXDDO3202K | X80 digital output, 32 channels, 24 V DC | 32
11 kV switchroom, M580 Ethernet remote drop (BMECRA31210 on BMEXBP1200) | 1, 2 | SWR-AI1 | BMXAMI0410 | X80 analogue input, 4 isolated channels | 4
President office station, Edge I/O island | 3 | PRS-DI1 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
President office station, Edge I/O island | 3 | PRS-DI2 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
President office station, Edge I/O island | 3 | PRS-DI3 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
President office station, Edge I/O island | 3 | PRS-DO1 | NTSDDO1602K | Edge I/O NTS digital output, 16 channels, 24 V DC, 0.5 A | 16
Prime Minister office station, Edge I/O island | 4 | PMS-DI1 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
Prime Minister office station, Edge I/O island | 4 | PMS-DI2 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
Prime Minister office station, Edge I/O island | 4 | PMS-DI3 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
Prime Minister office station, Edge I/O island | 4 | PMS-DO1 | NTSDDO1602K | Edge I/O NTS digital output, 16 channels, 24 V DC, 0.5 A | 16
BESS and inverter transformer yard, Edge I/O island | 5 | YRD-DI1 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
BESS and inverter transformer yard, Edge I/O island | 5 | YRD-DI2 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
Generator area, Edge I/O island | 6 | GEN-DI1 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
Generator area, Edge I/O island | 6 | GEN-DI2 | NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 16
Generator area, Edge I/O island | 6 | GEN-AI1 | To select | Edge I/O NTS analogue input, 4 channels | 4
Totals by location and type
Location | Type | Signals needed | Channels installed | Spare | Spare %
11 kV switchroom | DI |  | 128
11 kV switchroom | DO |  | 32
11 kV switchroom | AI |  | 4
President office station | DI |  | 48
President office station | DO |  | 16
Prime Minister office station | DI |  | 48
Prime Minister office station | DO |  | 16
BESS and inverter transformer yard | DI |  | 32
Generator area | DI |  | 32
Generator area | AI |  | 4
All locations | DI
All locations | DO
All locations | AI
Switchroom: one M580 Ethernet remote drop (BMEXBP1200, BMXCPS3020, BMECRA31210) holds all switchroom I/O, the analogue module and the BMXNOM0200 serial module; the CPU rack holds no I/O.
Each Edge I/O island: NTSNEC1200K network interface, NTSPFB1002HK power supply, the modules listed, terminal blocks per module, in an enclosure suited to its location (outdoor IP55 at the yard and generator area).
Office station islands also carry an NTSFMB0120K serial master for the ST260E RMU relay (Modbus RTU). Add one at the generator area if the generator controllers are RS485 only.
President and Prime Minister islands are identical; the offer labels both "PM office LVDB".

## IO Allocation
Tag | Description | Equipment | Type | Normal state / range | Alarm level | Operated by | Design row | Design module | Design channel | Schneider location | Schneider module | Module reference | Channel | Interface | Interposing relay
AH1-CB-OPEN | Circuit breaker open | 11 kV panel AH1, Generator incomer | DI | Status | Status | - | 1 | R1-DI01 | 1 | SWR | SWR-DI1 | BMXDDI3202K | 1 | Dry contact, wetted 24 V DC from the panel supply
AH1-CB-CLSD | Circuit breaker closed | 11 kV panel AH1, Generator incomer | DI | Status | Status | - | 1 | R1-DI01 | 2 | SWR | SWR-DI1 | BMXDDI3202K | 2 | Dry contact, wetted 24 V DC from the panel supply
AH1-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH1, Generator incomer | DI | Normally open | 1 | - | 1 | R1-DI01 | 3 | SWR | SWR-DI1 | BMXDDI3202K | 3 | Dry contact, wetted 24 V DC from the panel supply
AH1-ES-CLSD | Earth switch closed | 11 kV panel AH1, Generator incomer | DI | Status | Status | - | 1 | R1-DI01 | 4 | SWR | SWR-DI1 | BMXDDI3202K | 4 | Dry contact, wetted 24 V DC from the panel supply
AH1-LR-REM | Local/remote switch in remote | 11 kV panel AH1, Generator incomer | DI | Status | Status | - | 1 | R1-DI01 | 5 | SWR | SWR-DI1 | BMXDDI3202K | 5 | Dry contact, wetted 24 V DC from the panel supply
AH1-SPR-CHG | Closing spring charged | 11 kV panel AH1, Generator incomer | DI | Normally closed | 3 | - | 1 | R1-DI01 | 6 | SWR | SWR-DI1 | BMXDDI3202K | 6 | Dry contact, wetted 24 V DC from the panel supply
AH1-GAS-LOW | Gas pressure low | 11 kV panel AH1, Generator incomer | DI | Normally open | 2 | - | 1 | R1-DI01 | 7 | SWR | SWR-DI1 | BMXDDI3202K | 7 | Dry contact, wetted 24 V DC from the panel supply
AH1-RLY-OK | Protection relay healthy | 11 kV panel AH1, Generator incomer | DI | Normally closed | 2 | - | 1 | R1-DI01 | 8 | SWR | SWR-DI1 | BMXDDI3202K | 8 | Dry contact, wetted 24 V DC from the panel supply
AH1-AUX-OK | Control supply healthy | 11 kV panel AH1, Generator incomer | DI | Normally closed | 2 | - | 1 | R1-DI01 | 9 | SWR | SWR-DI1 | BMXDDI3202K | 9 | Dry contact, wetted 24 V DC from the panel supply
AH2-CB-OPEN | Circuit breaker open | 11 kV panel AH2, PV incomer | DI | Status | Status | - | 1 | R1-DI01 | 10 | SWR | SWR-DI1 | BMXDDI3202K | 10 | Dry contact, wetted 24 V DC from the panel supply
AH2-CB-CLSD | Circuit breaker closed | 11 kV panel AH2, PV incomer | DI | Status | Status | - | 1 | R1-DI01 | 11 | SWR | SWR-DI1 | BMXDDI3202K | 11 | Dry contact, wetted 24 V DC from the panel supply
AH2-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH2, PV incomer | DI | Normally open | 1 | - | 1 | R1-DI01 | 12 | SWR | SWR-DI1 | BMXDDI3202K | 12 | Dry contact, wetted 24 V DC from the panel supply
AH2-ES-CLSD | Earth switch closed | 11 kV panel AH2, PV incomer | DI | Status | Status | - | 1 | R1-DI01 | 13 | SWR | SWR-DI1 | BMXDDI3202K | 13 | Dry contact, wetted 24 V DC from the panel supply
AH2-LR-REM | Local/remote switch in remote | 11 kV panel AH2, PV incomer | DI | Status | Status | - | 1 | R1-DI01 | 14 | SWR | SWR-DI1 | BMXDDI3202K | 14 | Dry contact, wetted 24 V DC from the panel supply
AH2-SPR-CHG | Closing spring charged | 11 kV panel AH2, PV incomer | DI | Normally closed | 3 | - | 1 | R1-DI01 | 15 | SWR | SWR-DI1 | BMXDDI3202K | 15 | Dry contact, wetted 24 V DC from the panel supply
AH2-GAS-LOW | Gas pressure low | 11 kV panel AH2, PV incomer | DI | Normally open | 2 | - | 1 | R1-DI01 | 16 | SWR | SWR-DI1 | BMXDDI3202K | 16 | Dry contact, wetted 24 V DC from the panel supply
AH2-RLY-OK | Protection relay healthy | 11 kV panel AH2, PV incomer | DI | Normally closed | 2 | - | 1 | R1-DI02 | 1 | SWR | SWR-DI1 | BMXDDI3202K | 17 | Dry contact, wetted 24 V DC from the panel supply
AH2-AUX-OK | Control supply healthy | 11 kV panel AH2, PV incomer | DI | Normally closed | 2 | - | 1 | R1-DI02 | 2 | SWR | SWR-DI1 | BMXDDI3202K | 18 | Dry contact, wetted 24 V DC from the panel supply
AH3-CB-OPEN | Circuit breaker open | 11 kV panel AH3, BESS incomer | DI | Status | Status | - | 1 | R1-DI02 | 3 | SWR | SWR-DI1 | BMXDDI3202K | 19 | Dry contact, wetted 24 V DC from the panel supply
AH3-CB-CLSD | Circuit breaker closed | 11 kV panel AH3, BESS incomer | DI | Status | Status | - | 1 | R1-DI02 | 4 | SWR | SWR-DI1 | BMXDDI3202K | 20 | Dry contact, wetted 24 V DC from the panel supply
AH3-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH3, BESS incomer | DI | Normally open | 1 | - | 1 | R1-DI02 | 5 | SWR | SWR-DI1 | BMXDDI3202K | 21 | Dry contact, wetted 24 V DC from the panel supply
AH3-ES-CLSD | Earth switch closed | 11 kV panel AH3, BESS incomer | DI | Status | Status | - | 1 | R1-DI02 | 6 | SWR | SWR-DI1 | BMXDDI3202K | 22 | Dry contact, wetted 24 V DC from the panel supply
AH3-LR-REM | Local/remote switch in remote | 11 kV panel AH3, BESS incomer | DI | Status | Status | - | 1 | R1-DI02 | 7 | SWR | SWR-DI1 | BMXDDI3202K | 23 | Dry contact, wetted 24 V DC from the panel supply
AH3-SPR-CHG | Closing spring charged | 11 kV panel AH3, BESS incomer | DI | Normally closed | 3 | - | 1 | R1-DI02 | 8 | SWR | SWR-DI1 | BMXDDI3202K | 24 | Dry contact, wetted 24 V DC from the panel supply
AH3-GAS-LOW | Gas pressure low | 11 kV panel AH3, BESS incomer | DI | Normally open | 2 | - | 1 | R1-DI02 | 9 | SWR | SWR-DI2 | BMXDDI3202K | 1 | Dry contact, wetted 24 V DC from the panel supply
AH3-RLY-OK | Protection relay healthy | 11 kV panel AH3, BESS incomer | DI | Normally closed | 2 | - | 1 | R1-DI02 | 10 | SWR | SWR-DI2 | BMXDDI3202K | 2 | Dry contact, wetted 24 V DC from the panel supply
AH3-AUX-OK | Control supply healthy | 11 kV panel AH3, BESS incomer | DI | Normally closed | 2 | - | 1 | R1-DI02 | 11 | SWR | SWR-DI2 | BMXDDI3202K | 3 | Dry contact, wetted 24 V DC from the panel supply
AH4-CB-OPEN | Circuit breaker open | 11 kV panel AH4, President feeder | DI | Status | Status | - | 1 | R1-DI02 | 12 | SWR | SWR-DI2 | BMXDDI3202K | 4 | Dry contact, wetted 24 V DC from the panel supply
AH4-CB-CLSD | Circuit breaker closed | 11 kV panel AH4, President feeder | DI | Status | Status | - | 1 | R1-DI02 | 13 | SWR | SWR-DI2 | BMXDDI3202K | 5 | Dry contact, wetted 24 V DC from the panel supply
AH4-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH4, President feeder | DI | Normally open | 1 | - | 1 | R1-DI02 | 14 | SWR | SWR-DI2 | BMXDDI3202K | 6 | Dry contact, wetted 24 V DC from the panel supply
AH4-ES-CLSD | Earth switch closed | 11 kV panel AH4, President feeder | DI | Status | Status | - | 1 | R1-DI02 | 15 | SWR | SWR-DI2 | BMXDDI3202K | 7 | Dry contact, wetted 24 V DC from the panel supply
AH4-LR-REM | Local/remote switch in remote | 11 kV panel AH4, President feeder | DI | Status | Status | - | 1 | R1-DI02 | 16 | SWR | SWR-DI2 | BMXDDI3202K | 8 | Dry contact, wetted 24 V DC from the panel supply
AH4-SPR-CHG | Closing spring charged | 11 kV panel AH4, President feeder | DI | Normally closed | 3 | - | 1 | R1-DI03 | 1 | SWR | SWR-DI2 | BMXDDI3202K | 9 | Dry contact, wetted 24 V DC from the panel supply
AH4-GAS-LOW | Gas pressure low | 11 kV panel AH4, President feeder | DI | Normally open | 2 | - | 1 | R1-DI03 | 2 | SWR | SWR-DI2 | BMXDDI3202K | 10 | Dry contact, wetted 24 V DC from the panel supply
AH4-RLY-OK | Protection relay healthy | 11 kV panel AH4, President feeder | DI | Normally closed | 2 | - | 1 | R1-DI03 | 3 | SWR | SWR-DI2 | BMXDDI3202K | 11 | Dry contact, wetted 24 V DC from the panel supply
AH4-AUX-OK | Control supply healthy | 11 kV panel AH4, President feeder | DI | Normally closed | 2 | - | 1 | R1-DI03 | 4 | SWR | SWR-DI2 | BMXDDI3202K | 12 | Dry contact, wetted 24 V DC from the panel supply
AH5-CB-OPEN | Circuit breaker open | 11 kV panel AH5, Auxiliary transformer feeder | DI | Status | Status | - | 1 | R1-DI03 | 5 | SWR | SWR-DI2 | BMXDDI3202K | 13 | Dry contact, wetted 24 V DC from the panel supply
AH5-CB-CLSD | Circuit breaker closed | 11 kV panel AH5, Auxiliary transformer feeder | DI | Status | Status | - | 1 | R1-DI03 | 6 | SWR | SWR-DI2 | BMXDDI3202K | 14 | Dry contact, wetted 24 V DC from the panel supply
AH5-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH5, Auxiliary transformer feeder | DI | Normally open | 1 | - | 1 | R1-DI03 | 7 | SWR | SWR-DI2 | BMXDDI3202K | 15 | Dry contact, wetted 24 V DC from the panel supply
AH5-ES-CLSD | Earth switch closed | 11 kV panel AH5, Auxiliary transformer feeder | DI | Status | Status | - | 1 | R1-DI03 | 8 | SWR | SWR-DI2 | BMXDDI3202K | 16 | Dry contact, wetted 24 V DC from the panel supply
AH5-LR-REM | Local/remote switch in remote | 11 kV panel AH5, Auxiliary transformer feeder | DI | Status | Status | - | 1 | R1-DI03 | 9 | SWR | SWR-DI2 | BMXDDI3202K | 17 | Dry contact, wetted 24 V DC from the panel supply
AH5-SPR-CHG | Closing spring charged | 11 kV panel AH5, Auxiliary transformer feeder | DI | Normally closed | 3 | - | 1 | R1-DI03 | 10 | SWR | SWR-DI2 | BMXDDI3202K | 18 | Dry contact, wetted 24 V DC from the panel supply
AH5-GAS-LOW | Gas pressure low | 11 kV panel AH5, Auxiliary transformer feeder | DI | Normally open | 2 | - | 1 | R1-DI03 | 11 | SWR | SWR-DI2 | BMXDDI3202K | 19 | Dry contact, wetted 24 V DC from the panel supply
AH5-RLY-OK | Protection relay healthy | 11 kV panel AH5, Auxiliary transformer feeder | DI | Normally closed | 2 | - | 1 | R1-DI03 | 12 | SWR | SWR-DI2 | BMXDDI3202K | 20 | Dry contact, wetted 24 V DC from the panel supply
AH5-AUX-OK | Control supply healthy | 11 kV panel AH5, Auxiliary transformer feeder | DI | Normally closed | 2 | - | 1 | R1-DI03 | 13 | SWR | SWR-DI2 | BMXDDI3202K | 21 | Dry contact, wetted 24 V DC from the panel supply
AH6-CB-OPEN | Circuit breaker open | 11 kV panel AH6, Prime Minister feeder | DI | Status | Status | - | 1 | R1-DI03 | 14 | SWR | SWR-DI2 | BMXDDI3202K | 22 | Dry contact, wetted 24 V DC from the panel supply
AH6-CB-CLSD | Circuit breaker closed | 11 kV panel AH6, Prime Minister feeder | DI | Status | Status | - | 1 | R1-DI03 | 15 | SWR | SWR-DI2 | BMXDDI3202K | 23 | Dry contact, wetted 24 V DC from the panel supply
AH6-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH6, Prime Minister feeder | DI | Normally open | 1 | - | 1 | R1-DI03 | 16 | SWR | SWR-DI2 | BMXDDI3202K | 24 | Dry contact, wetted 24 V DC from the panel supply
AH6-ES-CLSD | Earth switch closed | 11 kV panel AH6, Prime Minister feeder | DI | Status | Status | - | 1 | R1-DI04 | 1 | SWR | SWR-DI3 | BMXDDI3202K | 1 | Dry contact, wetted 24 V DC from the panel supply
AH6-LR-REM | Local/remote switch in remote | 11 kV panel AH6, Prime Minister feeder | DI | Status | Status | - | 1 | R1-DI04 | 2 | SWR | SWR-DI3 | BMXDDI3202K | 2 | Dry contact, wetted 24 V DC from the panel supply
AH6-SPR-CHG | Closing spring charged | 11 kV panel AH6, Prime Minister feeder | DI | Normally closed | 3 | - | 1 | R1-DI04 | 3 | SWR | SWR-DI3 | BMXDDI3202K | 3 | Dry contact, wetted 24 V DC from the panel supply
AH6-GAS-LOW | Gas pressure low | 11 kV panel AH6, Prime Minister feeder | DI | Normally open | 2 | - | 1 | R1-DI04 | 4 | SWR | SWR-DI3 | BMXDDI3202K | 4 | Dry contact, wetted 24 V DC from the panel supply
AH6-RLY-OK | Protection relay healthy | 11 kV panel AH6, Prime Minister feeder | DI | Normally closed | 2 | - | 1 | R1-DI04 | 5 | SWR | SWR-DI3 | BMXDDI3202K | 5 | Dry contact, wetted 24 V DC from the panel supply
AH6-AUX-OK | Control supply healthy | 11 kV panel AH6, Prime Minister feeder | DI | Normally closed | 2 | - | 1 | R1-DI04 | 6 | SWR | SWR-DI3 | BMXDDI3202K | 6 | Dry contact, wetted 24 V DC from the panel supply
AH7-CB-OPEN | Circuit breaker open | 11 kV panel AH7, Spare feeder | DI | Status | Status | - | 1 | R1-DI04 | 7 | SWR | SWR-DI3 | BMXDDI3202K | 7 | Dry contact, wetted 24 V DC from the panel supply
AH7-CB-CLSD | Circuit breaker closed | 11 kV panel AH7, Spare feeder | DI | Status | Status | - | 1 | R1-DI04 | 8 | SWR | SWR-DI3 | BMXDDI3202K | 8 | Dry contact, wetted 24 V DC from the panel supply
AH7-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH7, Spare feeder | DI | Normally open | 1 | - | 1 | R1-DI04 | 9 | SWR | SWR-DI3 | BMXDDI3202K | 9 | Dry contact, wetted 24 V DC from the panel supply
AH7-ES-CLSD | Earth switch closed | 11 kV panel AH7, Spare feeder | DI | Status | Status | - | 1 | R1-DI04 | 10 | SWR | SWR-DI3 | BMXDDI3202K | 10 | Dry contact, wetted 24 V DC from the panel supply
AH7-LR-REM | Local/remote switch in remote | 11 kV panel AH7, Spare feeder | DI | Status | Status | - | 1 | R1-DI04 | 11 | SWR | SWR-DI3 | BMXDDI3202K | 11 | Dry contact, wetted 24 V DC from the panel supply
AH7-SPR-CHG | Closing spring charged | 11 kV panel AH7, Spare feeder | DI | Normally closed | 3 | - | 1 | R1-DI04 | 12 | SWR | SWR-DI3 | BMXDDI3202K | 12 | Dry contact, wetted 24 V DC from the panel supply
AH7-GAS-LOW | Gas pressure low | 11 kV panel AH7, Spare feeder | DI | Normally open | 2 | - | 1 | R1-DI04 | 13 | SWR | SWR-DI3 | BMXDDI3202K | 13 | Dry contact, wetted 24 V DC from the panel supply
AH7-RLY-OK | Protection relay healthy | 11 kV panel AH7, Spare feeder | DI | Normally closed | 2 | - | 1 | R1-DI04 | 14 | SWR | SWR-DI3 | BMXDDI3202K | 14 | Dry contact, wetted 24 V DC from the panel supply
AH7-AUX-OK | Control supply healthy | 11 kV panel AH7, Spare feeder | DI | Normally closed | 2 | - | 1 | R1-DI04 | 15 | SWR | SWR-DI3 | BMXDDI3202K | 15 | Dry contact, wetted 24 V DC from the panel supply
AH8-NER-EF | Earth fault current alarm | 11 kV panel AH8, neutral earthing resistor | DI | Normally open | 1 | - | 1 | R1-DI04 | 16 | SWR | SWR-DI3 | BMXDDI3202K | 16 | Dry contact, wetted 24 V DC from the panel supply
AH8-NER-TEMP | Resistor temperature high | 11 kV panel AH8, neutral earthing resistor | DI | Normally open | 2 | - | 1 | R1-DI05 | 1 | SWR | SWR-DI3 | BMXDDI3202K | 17 | Dry contact, wetted 24 V DC from the panel supply
AH8-AUX-OK | Panel supply healthy | 11 kV panel AH8, neutral earthing resistor | DI | Normally closed | 2 | - | 1 | R1-DI05 | 2 | SWR | SWR-DI3 | BMXDDI3202K | 18 | Dry contact, wetted 24 V DC from the panel supply
AH8-CB-OPEN | Circuit breaker open | 11 kV panel AH8, neutral earthing resistor | DI | Status | Status | - | 1 | R1-DI05 | 3 | SWR | SWR-DI3 | BMXDDI3202K | 19 | Dry contact, wetted 24 V DC from the panel supply
AH8-CB-CLSD | Circuit breaker closed | 11 kV panel AH8, neutral earthing resistor | DI | Status | Status | - | 1 | R1-DI05 | 4 | SWR | SWR-DI3 | BMXDDI3202K | 20 | Dry contact, wetted 24 V DC from the panel supply
AH8-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH8, neutral earthing resistor | DI | Normally open | 1 | - | 1 | R1-DI05 | 5 | SWR | SWR-DI3 | BMXDDI3202K | 21 | Dry contact, wetted 24 V DC from the panel supply
AH8-ES-CLSD | Earth switch closed | 11 kV panel AH8, neutral earthing resistor | DI | Status | Status | - | 1 | R1-DI05 | 6 | SWR | SWR-DI3 | BMXDDI3202K | 22 | Dry contact, wetted 24 V DC from the panel supply
AH8-GAS-LOW | Gas pressure low | 11 kV panel AH8, neutral earthing resistor | DI | Normally open | 2 | - | 1 | R1-DI05 | 7 | SWR | SWR-DI3 | BMXDDI3202K | 23 | Dry contact, wetted 24 V DC from the panel supply
T-AUX-OT-ALM | Oil temperature alarm | Auxiliary transformer 100 kVA | DI | Normally open | 3 | - | 2 | R2-DI01 | 1 | SWR | SWR-DI4 | BMXDDI3202K | 1 | Dry contact, wetted 24 V DC from the panel supply
T-AUX-OT-TRIP | Oil temperature trip | Auxiliary transformer 100 kVA | DI | Normally open | 1 | - | 2 | R2-DI01 | 2 | SWR | SWR-DI4 | BMXDDI3202K | 2 | Dry contact, wetted 24 V DC from the panel supply
T-AUX-WT-ALM | Winding temperature alarm | Auxiliary transformer 100 kVA | DI | Normally open | 3 | - | 2 | R2-DI01 | 3 | SWR | SWR-DI4 | BMXDDI3202K | 3 | Dry contact, wetted 24 V DC from the panel supply
T-AUX-WT-TRIP | Winding temperature trip | Auxiliary transformer 100 kVA | DI | Normally open | 1 | - | 2 | R2-DI01 | 4 | SWR | SWR-DI4 | BMXDDI3202K | 4 | Dry contact, wetted 24 V DC from the panel supply
T-AUX-PRD | Pressure relief device operated | Auxiliary transformer 100 kVA | DI | Normally open | 1 | - | 2 | R2-DI01 | 5 | SWR | SWR-DI4 | BMXDDI3202K | 5 | Dry contact, wetted 24 V DC from the panel supply
T-AUX-OL-LOW | Oil level low | Auxiliary transformer 100 kVA | DI | Normally open | 2 | - | 2 | R2-DI01 | 6 | SWR | SWR-DI4 | BMXDDI3202K | 6 | Dry contact, wetted 24 V DC from the panel supply
T-AUX-FUSE | HV fuse blown (XRNT-3A striker) | Auxiliary transformer 100 kVA | DI | Normally open | 1 | - | 2 | R2-DI02 | 7 | SWR | SWR-DI4 | BMXDDI3202K | 7 | Dry contact, wetted 24 V DC from the panel supply
AUXLV-INC-CLSD | Auxiliary LV incomer closed | Auxiliary supplies and UPS | DI | Status | Status | - | 2 | R2-DI01 | 7 | SWR | SWR-DI4 | BMXDDI3202K | 8 | Dry contact, wetted 24 V DC from the panel supply
AUXLV-INC-TRIP | Auxiliary LV incomer tripped | Auxiliary supplies and UPS | DI | Normally open | 2 | - | 2 | R2-DI01 | 8 | SWR | SWR-DI4 | BMXDDI3202K | 9 | Dry contact, wetted 24 V DC from the panel supply
AUXLV-SPD-FLT | Surge arrester failed | Auxiliary supplies and UPS | DI | Normally open | 3 | - | 2 | R2-DI01 | 9 | SWR | SWR-DI4 | BMXDDI3202K | 10 | Dry contact, wetted 24 V DC from the panel supply
UPS-ON-BATT | UPS on battery | Auxiliary supplies and UPS | DI | Normally open | 2 | - | 2 | R2-DI01 | 10 | SWR | SWR-DI4 | BMXDDI3202K | 11 | Dry contact, wetted 24 V DC from the panel supply
UPS-BATT-LOW | UPS battery low | Auxiliary supplies and UPS | DI | Normally open | 1 | - | 2 | R2-DI01 | 11 | SWR | SWR-DI4 | BMXDDI3202K | 12 | Dry contact, wetted 24 V DC from the panel supply
UPS-FLT | UPS fault | Auxiliary supplies and UPS | DI | Normally open | 2 | - | 2 | R2-DI01 | 12 | SWR | SWR-DI4 | BMXDDI3202K | 13 | Dry contact, wetted 24 V DC from the panel supply
UPS-BYPASS | UPS on bypass | Auxiliary supplies and UPS | DI | Normally open | 3 | - | 2 | R2-DI01 | 13 | SWR | SWR-DI4 | BMXDDI3202K | 14 | Dry contact, wetted 24 V DC from the panel supply
DC-CHG-FLT | DC charger fault | Auxiliary supplies and UPS | DI | Normally open | 2 | - | 2 | R2-DI01 | 14 | SWR | SWR-DI4 | BMXDDI3202K | 15 | Dry contact, wetted 24 V DC from the panel supply
DC-EARTH-FLT | DC earth fault | Auxiliary supplies and UPS | DI | Normally open | 2 | - | 2 | R2-DI01 | 15 | SWR | SWR-DI4 | BMXDDI3202K | 16 | Dry contact, wetted 24 V DC from the panel supply
DC-UV | DC bus undervoltage | Auxiliary supplies and UPS | DI | Normally open | 1 | - | 2 | R2-DI01 | 16 | SWR | SWR-DI4 | BMXDDI3202K | 17 | Dry contact, wetted 24 V DC from the panel supply
SWR-HVAC-FLT | Switchroom air conditioning fault | Auxiliary supplies and UPS | DI | Normally open | 3 | - | 2 | R2-DI02 | 1 | SWR | SWR-DI4 | BMXDDI3202K | 18 | Dry contact, wetted 24 V DC from the panel supply
SWR-TEMP-HI | Switchroom temperature high | Auxiliary supplies and UPS | DI | Normally open | 3 | - | 2 | R2-DI02 | 2 | SWR | SWR-DI4 | BMXDDI3202K | 19 | Dry contact, wetted 24 V DC from the panel supply
ESTOP-SWR | Plant emergency stop pressed, switchroom | Emergency stops, doors and I/O panels | DI | Normally open | 1 | - | 2 | R2-DI02 | 3 | SWR | SWR-DI4 | BMXDDI3202K | 20 | Dry contact, wetted 24 V DC from the panel supply
DOOR-SCADA | SCADA cabinet door open | Emergency stops, doors and I/O panels | DI | Normally open | 3 | - | 2 | R2-DI02 | 4 | SWR | SWR-DI4 | BMXDDI3202K | 21 | Dry contact, wetted 24 V DC from the panel supply
DOOR-SWR | Switchroom door open | Emergency stops, doors and I/O panels | DI | Normally open | 3 | - | 2 | R2-DI02 | 5 | SWR | SWR-DI4 | BMXDDI3202K | 22 | Dry contact, wetted 24 V DC from the panel supply
DOOR-GIS | 11 kV switchgear room door open | Emergency stops, doors and I/O panels | DI | Normally open | 3 | - | 2 | R2-DI02 | 6 | SWR | SWR-DI4 | BMXDDI3202K | 23 | Dry contact, wetted 24 V DC from the panel supply
AH1-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH1, Generator incomer | DO | Pulse | - | Operator | 1 | R1-CO01 | 1 | SWR | SWR-DO1 | BMXDDO3202K | 1 | Interposing relay IR01, contact in the breaker or switch control circuit | IR01
AH1-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH1, Generator incomer | DO | Pulse | - | Operator | 1 | R1-CO01 | 2 | SWR | SWR-DO1 | BMXDDO3202K | 2 | Interposing relay IR02, contact in the breaker or switch control circuit | IR02
AH2-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH2, PV incomer | DO | Pulse | - | Operator | 1 | R1-CO01 | 3 | SWR | SWR-DO1 | BMXDDO3202K | 3 | Interposing relay IR03, contact in the breaker or switch control circuit | IR03
AH2-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH2, PV incomer | DO | Pulse | - | Operator | 1 | R1-CO01 | 4 | SWR | SWR-DO1 | BMXDDO3202K | 4 | Interposing relay IR04, contact in the breaker or switch control circuit | IR04
AH3-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH3, BESS incomer | DO | Pulse | - | Operator | 1 | R1-CO01 | 5 | SWR | SWR-DO1 | BMXDDO3202K | 5 | Interposing relay IR05, contact in the breaker or switch control circuit | IR05
AH3-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH3, BESS incomer | DO | Pulse | - | Operator | 1 | R1-CO01 | 6 | SWR | SWR-DO1 | BMXDDO3202K | 6 | Interposing relay IR06, contact in the breaker or switch control circuit | IR06
AH4-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH4, President feeder | DO | Pulse | - | Operator | 1 | R1-CO01 | 7 | SWR | SWR-DO1 | BMXDDO3202K | 7 | Interposing relay IR07, contact in the breaker or switch control circuit | IR07
AH4-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH4, President feeder | DO | Pulse | - | Operator | 1 | R1-CO01 | 8 | SWR | SWR-DO1 | BMXDDO3202K | 8 | Interposing relay IR08, contact in the breaker or switch control circuit | IR08
AH5-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH5, Auxiliary transformer feeder | DO | Pulse | - | Operator | 1 | R1-CO01 | 9 | SWR | SWR-DO1 | BMXDDO3202K | 9 | Interposing relay IR09, contact in the breaker or switch control circuit | IR09
AH5-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH5, Auxiliary transformer feeder | DO | Pulse | - | Operator | 1 | R1-CO01 | 10 | SWR | SWR-DO1 | BMXDDO3202K | 10 | Interposing relay IR10, contact in the breaker or switch control circuit | IR10
AH6-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH6, Prime Minister feeder | DO | Pulse | - | Operator | 1 | R1-CO01 | 11 | SWR | SWR-DO1 | BMXDDO3202K | 11 | Interposing relay IR11, contact in the breaker or switch control circuit | IR11
AH6-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH6, Prime Minister feeder | DO | Pulse | - | Operator | 1 | R1-CO01 | 12 | SWR | SWR-DO1 | BMXDDO3202K | 12 | Interposing relay IR12, contact in the breaker or switch control circuit | IR12
AH7-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH7, Spare feeder | DO | Pulse | - | Operator | 1 | R1-CO02 | 1 | SWR | SWR-DO1 | BMXDDO3202K | 13 | Interposing relay IR13, contact in the breaker or switch control circuit | IR13
AH7-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH7, Spare feeder | DO | Pulse | - | Operator | 1 | R1-CO02 | 2 | SWR | SWR-DO1 | BMXDDO3202K | 14 | Interposing relay IR14, contact in the breaker or switch control circuit | IR14
SYS-BEACON | Critical alarm beacon and sounder | Control room alarm beacon | DO | De-energised | - | Automatic | 1 | R1-DO01 | 1 | SWR | SWR-DO1 | BMXDDO3202K | 17 | Interposing relay IR15, contact in the beacon or watchdog control circuit | IR15
SYS-CP-HEALTHY | Controller healthy output (watchdog) | SICAM CP-8050 | DO | Energised | - | Automatic | 1 | R1-DO01 | 2 | SWR | SWR-DO1 | BMXDDO3202K | 18 | Interposing relay IR16, contact in the beacon or watchdog control circuit | IR16
DC-110-V | 110 V DC bus voltage | Auxiliary supplies and UPS | AI | 4-20 mA = 0-150 V | 2 outside limits | - | 2 | R2-AI01 | 1 | SWR | SWR-AI1 | BMXAMI0410 | 1 | 4-20 mA, 4-20 mA = 0-150 V
DC-24-V | 24 V DC bus voltage | Auxiliary supplies and UPS | AI | 4-20 mA = 0-36 V | 2 outside limits | - | 2 | R2-AI01 | 2 | SWR | SWR-AI1 | BMXAMI0410 | 2 | 4-20 mA, 4-20 mA = 0-36 V
PRS-RS1-OPEN | Ring switch 1 open | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 1 | PRS | PRS-DI1 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
PRS-RS1-CLSD | Ring switch 1 closed | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 2 | PRS | PRS-DI1 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
PRS-RS1-ES | Ring switch 1 earth switch closed | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 3 | PRS | PRS-DI1 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
PRS-RS2-OPEN | Ring switch 2 open | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 4 | PRS | PRS-DI1 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
PRS-RS2-CLSD | Ring switch 2 closed | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 5 | PRS | PRS-DI1 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
PRS-RS2-ES | Ring switch 2 earth switch closed | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 6 | PRS | PRS-DI1 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
PRS-CB-OPEN | Transformer breaker open | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 7 | PRS | PRS-DI1 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
PRS-CB-CLSD | Transformer breaker closed | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 8 | PRS | PRS-DI1 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
PRS-CB-ES | Transformer breaker earth switch closed | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 9 | PRS | PRS-DI1 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
PRS-CB-TRIP | Transformer breaker tripped by ST260E | President station RMU | DI | Normally open | 1 | - | 3 | R3-DI01 | 10 | PRS | PRS-DI1 | NTSDDI1602XK | 10 | Dry contact, wetted 24 V DC from the panel supply
PRS-GAS-LOW | RMU gas pressure low | President station RMU | DI | Normally open | 2 | - | 3 | R3-DI01 | 11 | PRS | PRS-DI1 | NTSDDI1602XK | 11 | Dry contact, wetted 24 V DC from the panel supply
PRS-LR-REM | RMU local/remote in remote | President station RMU | DI | Status | Status | - | 3 | R3-DI01 | 12 | PRS | PRS-DI1 | NTSDDI1602XK | 12 | Dry contact, wetted 24 V DC from the panel supply
PRS-FPI | Fault passage indicator operated | President station RMU | DI | Normally open | 2 | - | 3 | R3-DI01 | 13 | PRS | PRS-DI2 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
PRS-TX-OT-ALM | Oil temperature alarm | President station transformer 630 kVA | DI | Normally open | 3 | - | 3 | R3-DI01 | 14 | PRS | PRS-DI2 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
PRS-TX-OT-TRIP | Oil temperature trip | President station transformer 630 kVA | DI | Normally open | 1 | - | 3 | R3-DI01 | 15 | PRS | PRS-DI2 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
PRS-TX-WT-ALM | Winding temperature alarm | President station transformer 630 kVA | DI | Normally open | 3 | - | 3 | R3-DI01 | 16 | PRS | PRS-DI2 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
PRS-TX-WT-TRIP | Winding temperature trip | President station transformer 630 kVA | DI | Normally open | 1 | - | 3 | R3-DI02 | 1 | PRS | PRS-DI2 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
PRS-TX-PRD | Pressure relief device operated | President station transformer 630 kVA | DI | Normally open | 1 | - | 3 | R3-DI02 | 2 | PRS | PRS-DI2 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
PRS-TX-OL-LOW | Oil level low | President station transformer 630 kVA | DI | Normally open | 2 | - | 3 | R3-DI02 | 3 | PRS | PRS-DI2 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-INC-CLSD | LV incomer closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 4 | PRS | PRS-DI2 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-INC-TRIP | LV incomer tripped | President station LVDB | DI | Normally open | 2 | - | 3 | R3-DI02 | 5 | PRS | PRS-DI2 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F01-CLSD | Outgoing way 1 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 6 | PRS | PRS-DI2 | NTSDDI1602XK | 10 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F02-CLSD | Outgoing way 2 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 7 | PRS | PRS-DI2 | NTSDDI1602XK | 11 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F03-CLSD | Outgoing way 3 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 8 | PRS | PRS-DI2 | NTSDDI1602XK | 12 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F04-CLSD | Outgoing way 4 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 9 | PRS | PRS-DI3 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F05-CLSD | Outgoing way 5 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 10 | PRS | PRS-DI3 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F06-CLSD | Outgoing way 6 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 11 | PRS | PRS-DI3 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F07-CLSD | Outgoing way 7 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 12 | PRS | PRS-DI3 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F08-CLSD | Outgoing way 8 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 13 | PRS | PRS-DI3 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F09-CLSD | Outgoing way 9 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 14 | PRS | PRS-DI3 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-F10-CLSD | Outgoing way 10 closed | President station LVDB | DI | Status | Status | - | 3 | R3-DI02 | 15 | PRS | PRS-DI3 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
PRS-LV-SPD-FLT | Surge arrester failed | President station LVDB | DI | Normally open | 3 | - | 3 | R3-DI02 | 16 | PRS | PRS-DI3 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
PRS-PNL-SUP-OK | I/O panel supply healthy | President station LVDB | DI | Normally closed | 2 | - | 3 | R3-DI03 | 1 | PRS | PRS-DI3 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
PRS-UPS-ON-BATT | RMU UPS 2 kVA on battery | President station RMU | DI | Normally open | 2 | - | 3 | R3-DI03 | 2 | PRS | PRS-DI3 | NTSDDI1602XK | 10 | Dry contact, wetted 24 V DC from the panel supply
PRS-UPS-FLT | RMU UPS 2 kVA fault | President station RMU | DI | Normally open | 2 | - | 3 | R3-DI03 | 3 | PRS | PRS-DI3 | NTSDDI1602XK | 11 | Dry contact, wetted 24 V DC from the panel supply
PRS-RS1-OPEN-CMD | Open ring switch 1 | President station RMU | DO | Pulse | - | Operator | 3 | R3-CO01 | 1 | PRS | PRS-DO1 | NTSDDO1602K | 1 | Interposing relay IR17, contact in the breaker or switch control circuit | IR17
PRS-RS1-CLOSE-CMD | Close ring switch 1 | President station RMU | DO | Pulse | - | Operator | 3 | R3-CO01 | 2 | PRS | PRS-DO1 | NTSDDO1602K | 2 | Interposing relay IR18, contact in the breaker or switch control circuit | IR18
PRS-RS2-OPEN-CMD | Open ring switch 2 | President station RMU | DO | Pulse | - | Operator | 3 | R3-CO01 | 3 | PRS | PRS-DO1 | NTSDDO1602K | 3 | Interposing relay IR19, contact in the breaker or switch control circuit | IR19
PRS-RS2-CLOSE-CMD | Close ring switch 2 | President station RMU | DO | Pulse | - | Operator | 3 | R3-CO01 | 4 | PRS | PRS-DO1 | NTSDDO1602K | 4 | Interposing relay IR20, contact in the breaker or switch control circuit | IR20
PRS-CB-OPEN-CMD | Open transformer breaker | President station RMU | DO | Pulse | - | Operator | 3 | R3-CO01 | 5 | PRS | PRS-DO1 | NTSDDO1602K | 5 | Interposing relay IR21, contact in the breaker or switch control circuit | IR21
PRS-CB-CLOSE-CMD | Close transformer breaker | President station RMU | DO | Pulse | - | Operator | 3 | R3-CO01 | 6 | PRS | PRS-DO1 | NTSDDO1602K | 6 | Interposing relay IR22, contact in the breaker or switch control circuit | IR22
PRS-LV-INC-OPEN-CMD | Open LV incomer | President station LVDB | DO | Pulse | - | Operator | 3 | R3-CO01 | 7 | PRS | PRS-DO1 | NTSDDO1602K | 7 | Interposing relay IR23, contact in the breaker or switch control circuit | IR23
PRS-LV-INC-CLOSE-CMD | Close LV incomer | President station LVDB | DO | Pulse | - | Operator | 3 | R3-CO01 | 8 | PRS | PRS-DO1 | NTSDDO1602K | 8 | Interposing relay IR24, contact in the breaker or switch control circuit | IR24
PMS-RS1-OPEN | Ring switch 1 open | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 1 | PMS | PMS-DI1 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
PMS-RS1-CLSD | Ring switch 1 closed | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 2 | PMS | PMS-DI1 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
PMS-RS1-ES | Ring switch 1 earth switch closed | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 3 | PMS | PMS-DI1 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
PMS-RS2-OPEN | Ring switch 2 open | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 4 | PMS | PMS-DI1 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
PMS-RS2-CLSD | Ring switch 2 closed | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 5 | PMS | PMS-DI1 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
PMS-RS2-ES | Ring switch 2 earth switch closed | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 6 | PMS | PMS-DI1 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
PMS-CB-OPEN | Transformer breaker open | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 7 | PMS | PMS-DI1 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
PMS-CB-CLSD | Transformer breaker closed | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 8 | PMS | PMS-DI1 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
PMS-CB-ES | Transformer breaker earth switch closed | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 9 | PMS | PMS-DI1 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
PMS-CB-TRIP | Transformer breaker tripped by ST260E | Prime Minister station RMU | DI | Normally open | 1 | - | 4 | R4-DI01 | 10 | PMS | PMS-DI1 | NTSDDI1602XK | 10 | Dry contact, wetted 24 V DC from the panel supply
PMS-GAS-LOW | RMU gas pressure low | Prime Minister station RMU | DI | Normally open | 2 | - | 4 | R4-DI01 | 11 | PMS | PMS-DI1 | NTSDDI1602XK | 11 | Dry contact, wetted 24 V DC from the panel supply
PMS-LR-REM | RMU local/remote in remote | Prime Minister station RMU | DI | Status | Status | - | 4 | R4-DI01 | 12 | PMS | PMS-DI1 | NTSDDI1602XK | 12 | Dry contact, wetted 24 V DC from the panel supply
PMS-FPI | Fault passage indicator operated | Prime Minister station RMU | DI | Normally open | 2 | - | 4 | R4-DI01 | 13 | PMS | PMS-DI2 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
PMS-TX-OT-ALM | Oil temperature alarm | Prime Minister station transformer 630 kVA | DI | Normally open | 3 | - | 4 | R4-DI01 | 14 | PMS | PMS-DI2 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
PMS-TX-OT-TRIP | Oil temperature trip | Prime Minister station transformer 630 kVA | DI | Normally open | 1 | - | 4 | R4-DI01 | 15 | PMS | PMS-DI2 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
PMS-TX-WT-ALM | Winding temperature alarm | Prime Minister station transformer 630 kVA | DI | Normally open | 3 | - | 4 | R4-DI01 | 16 | PMS | PMS-DI2 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
PMS-TX-WT-TRIP | Winding temperature trip | Prime Minister station transformer 630 kVA | DI | Normally open | 1 | - | 4 | R4-DI02 | 1 | PMS | PMS-DI2 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
PMS-TX-PRD | Pressure relief device operated | Prime Minister station transformer 630 kVA | DI | Normally open | 1 | - | 4 | R4-DI02 | 2 | PMS | PMS-DI2 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
PMS-TX-OL-LOW | Oil level low | Prime Minister station transformer 630 kVA | DI | Normally open | 2 | - | 4 | R4-DI02 | 3 | PMS | PMS-DI2 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-INC-CLSD | LV incomer closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 4 | PMS | PMS-DI2 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-INC-TRIP | LV incomer tripped | Prime Minister station LVDB | DI | Normally open | 2 | - | 4 | R4-DI02 | 5 | PMS | PMS-DI2 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F01-CLSD | Outgoing way 1 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 6 | PMS | PMS-DI2 | NTSDDI1602XK | 10 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F02-CLSD | Outgoing way 2 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 7 | PMS | PMS-DI2 | NTSDDI1602XK | 11 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F03-CLSD | Outgoing way 3 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 8 | PMS | PMS-DI2 | NTSDDI1602XK | 12 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F04-CLSD | Outgoing way 4 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 9 | PMS | PMS-DI3 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F05-CLSD | Outgoing way 5 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 10 | PMS | PMS-DI3 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F06-CLSD | Outgoing way 6 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 11 | PMS | PMS-DI3 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F07-CLSD | Outgoing way 7 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 12 | PMS | PMS-DI3 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F08-CLSD | Outgoing way 8 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 13 | PMS | PMS-DI3 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F09-CLSD | Outgoing way 9 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 14 | PMS | PMS-DI3 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-F10-CLSD | Outgoing way 10 closed | Prime Minister station LVDB | DI | Status | Status | - | 4 | R4-DI02 | 15 | PMS | PMS-DI3 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
PMS-LV-SPD-FLT | Surge arrester failed | Prime Minister station LVDB | DI | Normally open | 3 | - | 4 | R4-DI02 | 16 | PMS | PMS-DI3 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
PMS-PNL-SUP-OK | I/O panel supply healthy | Prime Minister station LVDB | DI | Normally closed | 2 | - | 4 | R4-DI03 | 1 | PMS | PMS-DI3 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
PMS-UPS-ON-BATT | RMU UPS 2 kVA on battery | Prime Minister station RMU | DI | Normally open | 2 | - | 4 | R4-DI03 | 2 | PMS | PMS-DI3 | NTSDDI1602XK | 10 | Dry contact, wetted 24 V DC from the panel supply
PMS-UPS-FLT | RMU UPS 2 kVA fault | Prime Minister station RMU | DI | Normally open | 2 | - | 4 | R4-DI03 | 3 | PMS | PMS-DI3 | NTSDDI1602XK | 11 | Dry contact, wetted 24 V DC from the panel supply
PMS-RS1-OPEN-CMD | Open ring switch 1 | Prime Minister station RMU | DO | Pulse | - | Operator | 4 | R4-CO01 | 1 | PMS | PMS-DO1 | NTSDDO1602K | 1 | Interposing relay IR25, contact in the breaker or switch control circuit | IR25
PMS-RS1-CLOSE-CMD | Close ring switch 1 | Prime Minister station RMU | DO | Pulse | - | Operator | 4 | R4-CO01 | 2 | PMS | PMS-DO1 | NTSDDO1602K | 2 | Interposing relay IR26, contact in the breaker or switch control circuit | IR26
PMS-RS2-OPEN-CMD | Open ring switch 2 | Prime Minister station RMU | DO | Pulse | - | Operator | 4 | R4-CO01 | 3 | PMS | PMS-DO1 | NTSDDO1602K | 3 | Interposing relay IR27, contact in the breaker or switch control circuit | IR27
PMS-RS2-CLOSE-CMD | Close ring switch 2 | Prime Minister station RMU | DO | Pulse | - | Operator | 4 | R4-CO01 | 4 | PMS | PMS-DO1 | NTSDDO1602K | 4 | Interposing relay IR28, contact in the breaker or switch control circuit | IR28
PMS-CB-OPEN-CMD | Open transformer breaker | Prime Minister station RMU | DO | Pulse | - | Operator | 4 | R4-CO01 | 5 | PMS | PMS-DO1 | NTSDDO1602K | 5 | Interposing relay IR29, contact in the breaker or switch control circuit | IR29
PMS-CB-CLOSE-CMD | Close transformer breaker | Prime Minister station RMU | DO | Pulse | - | Operator | 4 | R4-CO01 | 6 | PMS | PMS-DO1 | NTSDDO1602K | 6 | Interposing relay IR30, contact in the breaker or switch control circuit | IR30
PMS-LV-INC-OPEN-CMD | Open LV incomer | Prime Minister station LVDB | DO | Pulse | - | Operator | 4 | R4-CO01 | 7 | PMS | PMS-DO1 | NTSDDO1602K | 7 | Interposing relay IR31, contact in the breaker or switch control circuit | IR31
PMS-LV-INC-CLOSE-CMD | Close LV incomer | Prime Minister station LVDB | DO | Pulse | - | Operator | 4 | R4-CO01 | 8 | PMS | PMS-DO1 | NTSDDO1602K | 8 | Interposing relay IR32, contact in the breaker or switch control circuit | IR32
T-INV-OT-ALM | Oil temperature alarm | Inverter transformer | DI | Normally open | 3 | - | 5 | R5-DI01 | 1 | YRD | YRD-DI1 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
T-INV-OT-TRIP | Oil temperature trip | Inverter transformer | DI | Normally open | 1 | - | 5 | R5-DI01 | 2 | YRD | YRD-DI1 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
T-INV-WT-ALM | Winding temperature alarm | Inverter transformer | DI | Normally open | 3 | - | 5 | R5-DI01 | 3 | YRD | YRD-DI1 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
T-INV-WT-TRIP | Winding temperature trip | Inverter transformer | DI | Normally open | 1 | - | 5 | R5-DI01 | 4 | YRD | YRD-DI1 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
T-INV-PRD | Pressure relief device operated | Inverter transformer | DI | Normally open | 1 | - | 5 | R5-DI01 | 5 | YRD | YRD-DI1 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
T-INV-OL-LOW | Oil level low | Inverter transformer | DI | Normally open | 2 | - | 5 | R5-DI01 | 6 | YRD | YRD-DI1 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
PV-ACB-CLSD | PV main LV breaker (ACB 1250 A) closed | PV LV switchboard 0.8 kV (AC combiner) | DI | Status | Status | - | 5 | R5-DI02 | 3 | YRD | YRD-DI1 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
PV-ACB-TRIP | PV main LV breaker (ACB 1250 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | DI | Normally open | 1 | - | 5 | R5-DI02 | 4 | YRD | YRD-DI1 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
NB01-MCCB-TRIP | Inverter NB01 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | DI | Normally open | 2 | - | 5 | R5-DI02 | 5 | YRD | YRD-DI1 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
NB02-MCCB-TRIP | Inverter NB02 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | DI | Normally open | 2 | - | 5 | R5-DI02 | 6 | YRD | YRD-DI1 | NTSDDI1602XK | 10 | Dry contact, wetted 24 V DC from the panel supply
NB03-MCCB-TRIP | Inverter NB03 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | DI | Normally open | 2 | - | 5 | R5-DI02 | 7 | YRD | YRD-DI1 | NTSDDI1602XK | 11 | Dry contact, wetted 24 V DC from the panel supply
NB04-MCCB-TRIP | Inverter NB04 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | DI | Normally open | 2 | - | 5 | R5-DI02 | 8 | YRD | YRD-DI1 | NTSDDI1602XK | 12 | Dry contact, wetted 24 V DC from the panel supply
BESS-ACB-CLSD | Battery main LV breaker (ACB 1000 A) closed | BESS LV breaker 0.69 kV | DI | Status | Status | - | 5 | R5-DI02 | 9 | YRD | YRD-DI1 | NTSDDI1602XK | 13 | Dry contact, wetted 24 V DC from the panel supply
BESS-ACB-TRIP | Battery main LV breaker (ACB 1000 A) tripped | BESS LV breaker 0.69 kV | DI | Normally open | 1 | - | 5 | R5-DI02 | 10 | YRD | YRD-DI2 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
FIRE-PREALM | Pre-alarm | Fire detection and suppression panel | DI | Normally open | 2 | - | 5 | R5-DI01 | 7 | YRD | YRD-DI2 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
FIRE-ALM | Fire alarm | Fire detection and suppression panel | DI | Normally open | 1 | - | 5 | R5-DI01 | 8 | YRD | YRD-DI2 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
FIRE-FLT | System fault | Fire detection and suppression panel | DI | Normally open | 2 | - | 5 | R5-DI01 | 9 | YRD | YRD-DI2 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
FIRE-REL | Suppression released | Fire detection and suppression panel | DI | Normally open | 1 | - | 5 | R5-DI01 | 10 | YRD | YRD-DI2 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
FIRE-AGENT-LOW | Agent pressure low | Fire detection and suppression panel | DI | Normally open | 2 | - | 5 | R5-DI01 | 11 | YRD | YRD-DI2 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
FIRE-ISOL | System isolated | Fire detection and suppression panel | DI | Normally open | 2 | - | 5 | R5-DI01 | 12 | YRD | YRD-DI2 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
FIRE-MAN-REL | Manual release activated | Fire detection and suppression panel | DI | Normally open | 1 | - | 5 | R5-DI01 | 13 | YRD | YRD-DI2 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
FIRE-PSU-FLT | Panel supply fault | Fire detection and suppression panel | DI | Normally open | 2 | - | 5 | R5-DI01 | 14 | YRD | YRD-DI2 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
ESTOP-BESS | Plant emergency stop pressed, BESS area | Emergency stops, doors and I/O panels | DI | Normally open | 1 | - | 5 | R5-DI01 | 15 | YRD | YRD-DI2 | NTSDDI1602XK | 10 | Dry contact, wetted 24 V DC from the panel supply
DOOR-BESS | BESS container door open | Emergency stops, doors and I/O panels | DI | Normally open | 3 | - | 5 | R5-DI01 | 16 | YRD | YRD-DI2 | NTSDDI1602XK | 11 | Dry contact, wetted 24 V DC from the panel supply
YARD-PNL-SUP-OK | Yard I/O panel supply healthy | Emergency stops, doors and I/O panels | DI | Normally closed | 2 | - | 5 | R5-DI02 | 1 | YRD | YRD-DI2 | NTSDDI1602XK | 12 | Dry contact, wetted 24 V DC from the panel supply
YARD-PNL-DOOR | Yard I/O panel door open | Emergency stops, doors and I/O panels | DI | Normally open | 3 | - | 5 | R5-DI02 | 2 | YRD | YRD-DI2 | NTSDDI1602XK | 13 | Dry contact, wetted 24 V DC from the panel supply
T-DG-OT-ALM | Oil temperature alarm | Generator step-up transformer | DI | Normally open | 3 | - | 6 | R6-DI01 | 1 | GEN | GEN-DI1 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
T-DG-OT-TRIP | Oil temperature trip | Generator step-up transformer | DI | Normally open | 1 | - | 6 | R6-DI01 | 2 | GEN | GEN-DI1 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
T-DG-WT-ALM | Winding temperature alarm | Generator step-up transformer | DI | Normally open | 3 | - | 6 | R6-DI01 | 3 | GEN | GEN-DI1 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
T-DG-WT-TRIP | Winding temperature trip | Generator step-up transformer | DI | Normally open | 1 | - | 6 | R6-DI01 | 4 | GEN | GEN-DI1 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
T-DG-PRD | Pressure relief device operated | Generator step-up transformer | DI | Normally open | 1 | - | 6 | R6-DI01 | 5 | GEN | GEN-DI1 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
T-DG-OL-LOW | Oil level low | Generator step-up transformer | DI | Normally open | 2 | - | 6 | R6-DI01 | 6 | GEN | GEN-DI1 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
GEN-ACB-CLSD | DG step-up transformer LV breaker closed | Generator step-up transformer | DI | Status | Status | - | 6 | R6-DI02 | 1 | GEN | GEN-DI1 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
GEN-ACB-TRIP | DG step-up transformer LV breaker tripped | Generator step-up transformer | DI | Normally open | 1 | - | 6 | R6-DI02 | 2 | GEN | GEN-DI1 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
DG1-GCB-CLSD | Generator breaker closed | Diesel generator DG1 | DI | Status | Status | - | 6 | R6-DI01 | 7 | GEN | GEN-DI1 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
DG1-COM-ALM | Common alarm | Diesel generator DG1 | DI | Normally open | 2 | - | 6 | R6-DI01 | 8 | GEN | GEN-DI2 | NTSDDI1602XK | 1 | Dry contact, wetted 24 V DC from the panel supply
DG1-ESTOP | Emergency stop active | Diesel generator DG1 | DI | Normally open | 1 | - | 6 | R6-DI01 | 9 | GEN | GEN-DI2 | NTSDDI1602XK | 2 | Dry contact, wetted 24 V DC from the panel supply
DG1-RUN | Engine running | Diesel generator DG1 | DI | Status | Status | - | 6 | R6-DI01 | 10 | GEN | GEN-DI2 | NTSDDI1602XK | 3 | Dry contact, wetted 24 V DC from the panel supply
DG2-GCB-CLSD | Generator breaker closed | Diesel generator DG2 | DI | Status | Status | - | 6 | R6-DI01 | 11 | GEN | GEN-DI2 | NTSDDI1602XK | 4 | Dry contact, wetted 24 V DC from the panel supply
DG2-COM-ALM | Common alarm | Diesel generator DG2 | DI | Normally open | 2 | - | 6 | R6-DI01 | 12 | GEN | GEN-DI2 | NTSDDI1602XK | 5 | Dry contact, wetted 24 V DC from the panel supply
DG2-ESTOP | Emergency stop active | Diesel generator DG2 | DI | Normally open | 1 | - | 6 | R6-DI01 | 13 | GEN | GEN-DI2 | NTSDDI1602XK | 6 | Dry contact, wetted 24 V DC from the panel supply
DG2-RUN | Engine running | Diesel generator DG2 | DI | Status | Status | - | 6 | R6-DI01 | 14 | GEN | GEN-DI2 | NTSDDI1602XK | 7 | Dry contact, wetted 24 V DC from the panel supply
GEN-PNL-SUP-OK | Generator I/O panel supply healthy | Emergency stops, doors and I/O panels | DI | Normally closed | 2 | - | 6 | R6-DI01 | 15 | GEN | GEN-DI2 | NTSDDI1602XK | 8 | Dry contact, wetted 24 V DC from the panel supply
GEN-PNL-DOOR | Generator I/O panel door open | Emergency stops, doors and I/O panels | DI | Normally open | 3 | - | 6 | R6-DI01 | 16 | GEN | GEN-DI2 | NTSDDI1602XK | 9 | Dry contact, wetted 24 V DC from the panel supply
DG1-FUEL | Fuel tank level | Diesel generator DG1 | AI | 4-20 mA = 0-100 % | 3 below 20 % | - | 6 | R6-AI01 | 1 | GEN | GEN-AI1 | NTS analogue input (to select) | 1 | 4-20 mA, 4-20 mA = 0-100 %
DG2-FUEL | Fuel tank level | Diesel generator DG2 | AI | 4-20 mA = 0-100 % | 3 below 20 % | - | 6 | R6-AI01 | 2 | GEN | GEN-AI1 | NTS analogue input (to select) | 2 | 4-20 mA, 4-20 mA = 0-100 %

## Changes to Offer
Changes against the Schneider offer
Quantities include one spare per module type, as in the offer. "Not priced" = in the offer PDF and drawing but not in the priced bill of material.
Reference | Description | Offer qty | Proposed qty | Change | Reason
HMIP67GD0F88BE7N00 | Industrial panel PC (no description in the offer) | 2 | 2 | Keep; clarify | Confirm model, and whether the SCADA runs on these PCs or on servers (Other Items, item 4).
HMIEMSE3PRT4KA | Machine SCADA Expert runtime, 4K tags | 2 | 2 | Keep | 707 tags (244 hardwired + 463 communication) fit in 4K.
HMIEMSEBT4KA | Machine SCADA Expert build-time, 4K tags | 1 | 1 | Keep
BMEXBP0800 | X80 8-slot Ethernet backplane (CPU rack) | 2 | 2 | Keep | CPU rack, no I/O. See Other Items, item 1 for hot standby.
BMXCPS3020 | X80 power supply 24-48 V DC | 3 | 3 | Keep | CPU rack, switchroom drop, spare.
BMEP582040 | M580 CPU | 2 | 2 | Keep or replace | Simplex as offered; the design requires a hot standby pair (Other Items, item 1).
BMENOC0311 | M580 Ethernet communication module | 2 | 2 | Keep
BMENOC0321 | M580 Ethernet module, IP forwarding | 1 | 1 | Keep
BMEXBP1200 | X80 12-slot Ethernet backplane (switchroom drop) | 1 | 1 | Keep | Holds CRA, 4 DI, 1 DO, 1 AI and the serial module.
BMECRA31210 | X80 Ethernet drop adapter | 1 | 1 | Keep
BMXDDI3202K | X80 digital input, 32 channels, 24 V DC | 5 | 5 | Same quantity, moved | All 4 in the switchroom drop (94 inputs on 128 channels) + 1 spare; none in the CPU rack.
BMXDDO3202K | X80 digital output, 32 channels, 24 V DC | 4 | 2 | Reduce by 2 | Switchroom has 16 outputs: 1 module + 1 spare.
BMXFCW303 | Pre-wired cable for 32-channel modules | 7 | 7 | Keep | One per 32-channel module including spares.
BMXAMI0410 | X80 analogue input, 4 isolated channels, with its terminal block | 0 | 2 | Add 2 | DC bus voltages 110 V and 24 V (4-20 mA); 1 + 1 spare.
BMXNOM0200 | X80 serial module, Modbus RTU | 1 | 1 | Keep; confirm use | State which switchroom devices it serves.
VW3A8306R10 | RS485 cable | 1 | 1 | Keep
MCSESM083F23F1 | Managed switch, 8 copper ports | 2 | 2 | Clarify | No fibre ports. Remote locations need fibre (Other Items, item 2).
NTSNEC1200K | Edge I/O network interface | 7 | 5 | Reduce by 2 | 4 islands (President, PM, yard, generators) + 1 spare.
NTSPFB1002HK | Edge I/O power supply module | 7 | 5 | Reduce by 2 | As above.
NTSXTB02030H | Terminal block for the power supply module | 12 | 8 | Reduce by 4 | 2 per island.
NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC | 19 | 11 | Reduce by 8 | President 3, PM 3, yard 2, generators 2, + 1 spare.
NTSXTB18001XH | Terminal block for NTSDDI1602XK | 18 | 10 | Reduce by 8 | One per input module in use.
NTSDDO1602K | Edge I/O NTS digital output, 16 channels, 24 V DC, 0.5 A | 7 | 3 | Reduce by 4 | President 1, PM 1 (8 commands each), + 1 spare.
NTSXTB18001H | Terminal block for NTSDDO1602K | 6 | 2 | Reduce by 4 | One per output module in use.
NTSFMB0120K | Edge I/O serial master, Modbus RTU | 6 | 2 | Reduce by 4 | ST260E relay at each office station. Add 1 at the generators only if their controllers are RS485.
NTSXTB12001H | Terminal block for NTSFMB0120K | 6 | 2 | Reduce by 4
To select | Edge I/O NTS analogue input, 4 x 4-20 mA, with terminal block | 0 | 2 | Add 2 | Generator fuel levels DG1 and DG2; 1 + 1 spare.
To select | Interposing relay, 24 V DC coil, contact rated for the 110 V DC control circuit, with base | 0 | 34 | Add 34 | 30 command relays (AH1-AH7 open/close, RMU and LV incomer commands at both stations) + beacon and watchdog + 2 spare.
To select | 24 V DC field supply for contact wetting, I/O and the X80/NTS power supplies | 0 | 5 | Add 5 | One per location; supplied from the 110 V DC station battery where available.
PVSCL60E | Schneider three-phase string inverter (not priced) | 4 | 0 | Remove | The plant has 4 Sungrow SG350HX inverters, read through the PLC box over Modbus TCP.
PAS600 + CL110 + TH110 | Panel servers with humidity and temperature sensors | 7 | 0 | Move to option | 7 panel servers, 7 humidity and 9 temperature sensors are not in the I/O list. Quote separately as an option for the client to decide.
REL50458 | Easergy P5M30 protection relay (not priced) | 8 | 0 | Clarify | The 11 kV relays may come with the switchgear. If Schneider supplies them, the P5M30 appears to be the motor variant; feeders normally use P5F30.
METSEPM5320 | PM5320 power meter (not priced) | 5 | 0 | Clarify | The design has 3 x PM5560 (President LVDB, PM LVDB, auxiliary board). State where 5 meters would go.
Lot | System design and commissioning | 1 | 1 | Requote | To the corrected scope.

## Other Items
Other items to quote or clarify
Requirements from the SCADA Design Report Rev 1 that the offer does not cover.
No. | Item | Requirement
1 | Controller redundancy | The design requires a hot standby controller pair (design report section 4). Quote M580 Hot Standby (two BMEH58 processors on hot standby racks, as described in the offer) with all I/O in the switchroom drop and the Edge I/O islands. State the switchover time. Keep the simplex CPU as a price option.
2 | Fibre network | The office stations, BESS yard and generator area are beyond the 100 m copper limit. Quote managed switches with SFP fibre ports in a ring, or state how the PLC and Edge I/O connect to the fibre ring of the design.
3 | Cybersecurity | Firewall with VPN for remote support (off by default), and time synchronisation (GPS/NTP). State the M580 and SCADA security settings used.
4 | SCADA | State whether the SCADA is redundant, where the historian runs and its retention, and confirm Operator and Admin roles, three alarm levels, the event log with user names, and report export.
5 | Communication interfaces | Confirm each interface and its points per sheet Comms Point List of the I/O list: 11 kV relays (IEC 61850 or Modbus TCP), EMS (Modbus TCP), PLC box (Modbus TCP), ST260E (Modbus RTU), power meters, weather logger, UPS, network devices (SNMP).
6 | Control authority | The embedded EMS dispatches PV, battery and generators. The PLC monitors, checks interlocks on remote commands and passes Admin settings to the EMS; it does not run plant dispatch sequences. Correct the offer text accordingly.
7 | Emergency stop | Hardwired only; the PLC and SCADA only display it. No software emergency stop.
8 | Enclosures and wiring | State who supplies the Edge I/O enclosures (outdoor IP55 at the yard and generator area), marshalling, interposing relay panels and field wiring.
9 | Commercial terms | State currency, validity, delivery time, payment terms, warranty and exclusions. The General Conditions section of the offer is empty.
10 | Offer text | Remove text from another project (treated-water process, IICATS, LIMS, Quantum RIO), complete the revision history and table of contents, and correct the second office island to the President station.