## Read Me
Villa Somalia Hybrid Plant: SCADA Device and I/O List
Project | Solarization of Villa Somalia, Mogadishu. 1,516 kWp PV, 3,340 kWh BESS, 2 diesel generators, 11 kV switchboard, 2 office transformer stations.
Status | Rev 2, 16 Oct 2026: control platform changed to Schneider Electric (Modicon M580 hot standby, Modicon X80 and Edge I/O NTS, EcoStruxure Machine SCADA Expert). Signals and tags as Rev 1. For client submission as Attachment B.
Controller | Two Schneider Electric Modicon M580 hot standby CPUs (A active, B standby) as plant controller and gateway. The embedded EMS keeps dispatch of PV, battery and generators.
SCADA | EcoStruxure Machine SCADA Expert on two SCADA stations (active and hot standby), linked to the controllers by Modbus TCP.
Sheets
Device List | Every device in the design: model, product or ordering number, quantity, location, interface and protocol to the controllers.
Protocol Summary | Device quantities per protocol, calculated from the Device List.
IO List | Every hardwired signal: tag, description, type, I/O location, Schneider module and channel, alarm level and who may operate it.
Datasheets | Register of every datasheet and software document for Attachment C, with where to download it and a Collected column.
IO Locations | The five I/O locations: the switchroom remote drop and four Edge I/O islands, their link to the controllers and the equipment wired to each.
IO Summary | Channels used and spare per I/O module, calculated from the IO List.
Comms Points | Typical signals read or written over communication links, per device type, with quantities. Replace with each vendor's point table.
Comms Point List | The Comms Points expanded to one row per signal, each with its own tag and alarm level, as used by the HMI.
Number status key
Checked | Product number found on a supplier listing or configuration document.
From memory - confirm | Ordering code from knowledge of the maker's catalogue; not checked online. Confirm with the distributor.
To confirm with supplier | Product exists but its number was not found. Take it from the supplier's quotation.
Existing (drawings) | Device already specified in drawing set VILLA_SOMALIA_05_10_2026.
TBC | Make or model unknown. Must come from the PV designer or the equipment supplier. Cells marked TBC are shaded yellow.
From the Schneider offer | Reference taken from Schneider Electric's Offer Proposal Villa Somalia, version 1, 16 Oct 2026. Confirm in the requote.
Assumptions
1 | Field contacts are dry contacts, wetted at 24 V DC from a field supply in each I/O panel. Breaker and switch commands drive interposing relays whose contacts switch the 110 V DC control circuit; the 24 V DC outputs never switch a coil directly.
2 | 11 kV breakers, RMU switches and LVDB incomers are motorised and accept remote open and close.
3 | The embedded EMS offers Modbus TCP. The PV inverter data reaches the controllers from the power line communication box, as shown on the existing communication sheet.
4 | Signal counts per device are typical values. They must be checked against the switchgear, RMU, transformer and fire panel terminal schedules.
5 | Measurements (current, voltage, power, energy) come over communication from relays, meters and the EMS, not hardwired.
6 | Spare capacity target is about 20% per I/O location.
7 | Field signals are collected at the nearest I/O location: switchroom remote drop (SWR), President and Prime Minister office stations (PRS, PMS), BESS and inverter transformer yard (YRD), generator area (GEN). The four islands connect over the fibre ring. Actual cable distances are not known yet.
Revision 1 changes (Siemens platform; replaced by Revision 2 where they differ)
1 | AH8: breaker open, closed, tripped, earth switch and gas pressure added (row 1). The 11 kV system is earthed only through AH8.
2 | LV main breakers added: PV ACB 1250 A and BESS ACB 1000 A (row 5), DG step-up transformer LV ACB (row 6).
3 | Combiner panels: trip of the four inverter AC MCCBs (row 5); battery combiner panel switch and fuse status through the EMS.
4 | Auxiliary transformer XRNT-3A fuse blown (row 2); RMU UPS 2 kVA on battery and fault at both office stations (rows 3, 4).
5 | 11 kV relays: trip circuit supervision (7), sensitive earth fault trip (6) and reverse power trip on AH1 added as communication points.
6 | Totals: 244 hardwired signals and 463 communication points. Overall spare is 27%; row 5 drops to 19% (6 of 32 channels), just under the 20% target: add a third DI-8112 there if more yard signals appear.
7 | Comms Point List sheet added. Devices D49 and D50 added to the Device List.
8 | Controller made redundant: two CP-8050 (A active, B hot standby), each with two power supplies, its own Ethernet interface, flash card and licences. I/O row 1 moved off the controller backplane onto its own CI-8532 so both controllers reach it. Communication points added for each controller's health and supplies, which controller is active, standby ready and switchover. Siemens to confirm the redundancy function, switchover time and how the I/O rows connect to both controllers.
Revision 2 changes
1 | Control platform changed from Siemens SICAM A8000 to Schneider Electric: Modicon M580 hot standby CPUs, X80 remote drop in the switchroom, Edge I/O NTS islands at the office stations, BESS yard and generator area, EcoStruxure Machine SCADA Expert on two SCADA stations.
2 | Same 244 hardwired signals and tags. I/O rows 1 to 6 become five I/O locations (rows 1 and 2 are one switchroom drop); module and channel columns now give the Schneider allocation, 32 interposing relays for the commands.
3 | Communication points: the six I/O row link points become five I/O location link points (CP-IO-SWR-OK to CP-IO-GEN-OK); controller points keep their tags. Total 462 communication points.
4 | Controller to SCADA link is Modbus TCP (was IEC 60870-5-104). ST260E relays are read by the Edge I/O serial masters instead of MGate gateways. 11 kV relays on Modbus TCP; IEC 61850 needs an added controller module.
5 | Device List sections B to E rebuilt for Schneider equipment (new IDs D18 to D59). Firewall, GPS time server and engineering laptop stay with other makers. IO Rows sheet renamed IO Locations; IO Summary, Protocol Summary and Datasheets rebuilt.

## Device List
ID | Group | Device | Manufacturer | Model | Product / ordering no. | Number status | Qty | Location | Physical interface | Protocol to the controllers | Primary protocol | Hardwired to I/O location | Notes
A. Plant equipment (existing or by others)
D01 | Plant | PV string inverters NB01 to NB04 | Sungrow | SG350HX | - | Existing (drawings) | 4 | PV field | AC power cable | Power line communication to the PLC box | Power line communication | - | Not connected to the controllers directly.
D02 | Plant | Power line communication box (PLC box) | Sungrow | TBC | TBC | TBC | 1 | Inverter MV station | Ethernet RJ45 | Modbus TCP (to confirm) | Modbus TCP | - | Converts inverter data to Ethernet. Get model and point table from the PV designer.
D03 | Plant | Embedded energy management system (EMS) | TBC | TBC | TBC | TBC | 1 | BESS / EMS area | Ethernet RJ45 | Modbus TCP (to confirm) | Modbus TCP | - | Dispatches PV, battery and generators. Only the controllers write settings to it.
D04 | Plant | Battery energy storage system, 3,340 kWh | Sungrow | ST3340UX | - | Existing (drawings) | 1 | BESS area | Ethernet (via EMS) | Through the EMS, Modbus TCP | Modbus TCP | - | Confirm whether battery data is read through the EMS or directly. Battery combiner panel status read through the EMS if available (rev 1).
D05 | Plant | Generator controllers DG1, DG2 | TBC | TBC | TBC | TBC | 2 | Generator area | Ethernet or RS485 | Modbus TCP, or Modbus RTU through an Edge I/O serial master | Modbus TCP | GEN | Breaker status, alarm, E-stop, running and fuel level also hardwired to the generator area I/O island.
D06 | Plant | 11 kV protection relays, panels AH1 to AH7 | TBC (switchgear supplier) | TBC | TBC | TBC | 7 | 11 kV switchroom | Ethernet, 2 ports preferred | Modbus TCP (IEC 61850 needs an IEC 61850 module on the controllers) | Modbus TCP | SWR | Dual-connect to both core switches if the relay has two ports.
D07 | Plant | Neutral earthing resistor panel AH8 | TBC (switchgear supplier) | - | - | TBC | 1 | 11 kV switchroom | Dry contacts | Hardwired | Hardwired | SWR | Breaker position, trip, earth switch and gas pressure also wired to the switchroom I/O (rev 1).
D08 | Plant | RMU protection relays | Per RMU supplier | ST260E | - | Existing (drawings) | 2 | President and PM stations | RS485 | Modbus RTU, through the Edge I/O serial master (NTSFMB0120K) | Modbus RTU | PRS, PMS | Confirm Modbus map with the RMU supplier. Read by the serial master on the office station Edge I/O island.
D09 | Plant | Transformers: inverter, DG step-up, 100 kVA auxiliary | TBC | - | - | TBC | 3 | Yard, generator area, switchroom | Dry contacts | Hardwired | Hardwired | YRD, GEN, SWR | Each wired to the nearest I/O location: inverter to the yard I/O island, DG step-up to the generator area I/O island, auxiliary to the switchroom I/O. Auxiliary transformer also has its XRNT-3A fuse striker wired to the switchroom I/O (rev 1).
D10 | Plant | Transformers 630 kVA, President and PM stations | TBC | - | - | TBC | 2 | Office stations | Dry contacts | Hardwired | Hardwired | PRS, PMS
D11 | Plant | Low-voltage distribution boards, 10-way | TBC | - | - | TBC | 2 | Office stations | Dry contacts + meter | Hardwired; meter on Modbus TCP | Hardwired | PRS, PMS
D12 | Plant | Fire detection and suppression panel | TBC | TBC | TBC | TBC | 1 | BESS area | Dry contacts | Hardwired | Hardwired | YRD | Also a direct hardwired trip to the battery, outside the SCADA.
D13 | Plant | UPS and auxiliary DC supplies | TBC | TBC | TBC | TBC | 1 | 11 kV switchroom | Ethernet or dry contacts | Modbus TCP or SNMP, plus contacts | Modbus TCP | SWR
D14 | Plant | Weather station data logger | Meteocontrol | blue'Log XM with Multi I/O and Fieldbus Ext | - | Existing (drawings) | 1 | Inverter MV station | Ethernet RJ45 | Modbus TCP | Modbus TCP | - | Collects the sensors below.
D15 | Plant | Pyranometer | Kipp & Zonen | SMP12-A | - | Existing (drawings) | 1 | Weather mast | RS485 to logger | Through the blue'Log | Through logger | -
D16 | Plant | Wind sensor | Gill Instruments | WindSonic RS485 | - | Existing (drawings) | 1 | Weather mast | RS485 to logger | Through the blue'Log | Through logger | -
D17 | Plant | Ambient and module temperature sensors | TBC | - | - | Existing (drawings) | 2 | Weather mast / PV array | Analogue to logger | Through the blue'Log | Through logger | -
D49 | Plant | LV main breakers: PV ACB 1250 A, BESS ACB 1000 A, DG step-up LV ACB; inverter AC MCCBs 400 A | TBC (switchboard supplier) | - | - | Existing (drawings) | 3 | Inverter MV station, BESS area, generator area | Dry contacts | Hardwired | Hardwired | YRD, GEN | Added rev 1. Position and trip of each main breaker; trip of the four inverter MCCBs (yard I/O island).
D50 | Plant | RMU UPS 2 kVA, 220 V AC | TBC (RMU supplier) | - | - | Existing (drawings) | 2 | President and PM stations | Dry contacts | Hardwired | Hardwired | PRS, PMS | Added rev 1. On battery and fault contacts.
B. Modicon M580 controllers and I/O (Schneider Electric)
D18 | Controller | Hot standby CPU, level 2, with remote and distributed I/O | Schneider Electric | Modicon M580 | BMEH582040 | To confirm with supplier | 2 | 11 kV switchroom, SCADA cabinet | Ethernet | Gateway for all protocols | Modbus TCP | - | Hot standby pair: controller A active, B standby, each in its own rack, linked by the hot standby link. The offer quotes the simplex BMEP582040; requote as hot standby. Schneider to confirm the switchover time.
D19 | Controller | Ethernet backplane, 6 slots, dual power supply (CPU racks) | Schneider Electric | Modicon X80 | BMEXBP0602 | To confirm with supplier | 2 | 11 kV switchroom, SCADA cabinet | - | - | N/A | - | One per CPU. Dual power supply racks are named in the offer for hot standby.
D20 | Controller | Redundant power supply, 24-48 V DC (CPU racks) | Schneider Electric | Modicon X80 | To select | To confirm with supplier | 4 | 11 kV switchroom, SCADA cabinet | - | - | N/A | - | Two per CPU rack. Reference to suit the supply voltage.
D21 | Controller | Ethernet communication module, 3 ports (device network) | Schneider Electric | Modicon M580 | BMENOC0311 | From the Schneider offer | 2 | 11 kV switchroom, SCADA cabinet | 3 x RJ45 | Modbus TCP, EtherNet/IP | N/A | - | One per CPU rack: relays, meters, EMS, PLC box, weather logger, Edge I/O islands.
D22 | Controller | Ethernet communication module with IP forwarding (control network) | Schneider Electric | Modicon M580 | BMENOC0321 | From the Schneider offer | 2 | 11 kV switchroom, SCADA cabinet | 3 x RJ45 | Modbus TCP | N/A | - | One per CPU rack: link to the SCADA stations; keeps the control and device networks apart.
D23 | Controller | Hot standby link transceivers and cable | Schneider Electric | Modicon M580 | To select | To confirm with supplier | 1 | 11 kV switchroom, SCADA cabinet | Fibre or copper | Hot standby link | N/A | - | Between CPU A and CPU B.
D24 | I/O | Ethernet backplane, 12 slots (switchroom drop) | Schneider Electric | Modicon X80 | BMEXBP1200 | From the Schneider offer | 1 | 11 kV switchroom, SCADA cabinet | - | - | N/A | SWR
D25 | I/O | Power supply, 24-48 V DC, 32 W (switchroom drop) | Schneider Electric | Modicon X80 | BMXCPS3020 | From the Schneider offer | 1 | 11 kV switchroom, SCADA cabinet | - | - | N/A | SWR
D26 | I/O | Ethernet remote drop adapter | Schneider Electric | Modicon X80 | BMECRA31210 | From the Schneider offer | 1 | 11 kV switchroom, SCADA cabinet | 2 x RJ45 | M580 Ethernet remote I/O | M580 Ethernet remote I/O | SWR | Switchroom drop on the remote I/O network, reached by both controllers.
D27 | I/O | Digital input, 32 channels, 24 V DC | Schneider Electric | Modicon X80 | BMXDDI3202K | From the Schneider offer | 4 | 11 kV switchroom, SCADA cabinet | Pre-wired cable | M580 Ethernet remote I/O | M580 Ethernet remote I/O | SWR | 94 switchroom inputs. Dry contacts wetted at 24 V DC.
D28 | I/O | Digital output, 32 channels, 24 V DC | Schneider Electric | Modicon X80 | BMXDDO3202K | From the Schneider offer | 1 | 11 kV switchroom, SCADA cabinet | Pre-wired cable | M580 Ethernet remote I/O | M580 Ethernet remote I/O | SWR | 14 breaker commands, alarm beacon and watchdog, each through an interposing relay.
D29 | I/O | Analogue input, 4 isolated channels | Schneider Electric | Modicon X80 | BMXAMI0410 | To confirm with supplier | 1 | 11 kV switchroom, SCADA cabinet | Terminal block | M580 Ethernet remote I/O | M580 Ethernet remote I/O | SWR | 110 V and 24 V DC bus voltages, 4-20 mA.
D30 | I/O | Pre-wired cable for 32-channel modules, 3 m | Schneider Electric | Modicon X80 | BMXFCW303 | From the Schneider offer | 5 | 11 kV switchroom, SCADA cabinet | - | - | N/A | SWR
D31 | I/O | Serial link module, Modbus RTU | Schneider Electric | Modicon X80 | BMXNOM0200 | From the Schneider offer | 1 | 11 kV switchroom, SCADA cabinet | RS485 | Modbus RTU | Modbus RTU | - | For switchroom devices with RS485 only. Confirm use.
D32 | I/O | Edge I/O network interface, 2 x RJ45 | Schneider Electric | Modicon Edge I/O NTS | NTSNEC1200K | From the Schneider offer | 4 | Office stations, BESS yard, generator area | 2 x RJ45 | EtherNet/IP | EtherNet/IP | PRS, PMS, YRD, GEN | One per island.
D33 | I/O | Edge I/O power supply module, 24 V DC | Schneider Electric | Modicon Edge I/O NTS | NTSPFB1002HK | From the Schneider offer | 4 | Office stations, BESS yard, generator area | - | - | N/A | PRS, PMS, YRD, GEN
D34 | I/O | Edge I/O digital input, 16 channels, 24 V DC | Schneider Electric | Modicon Edge I/O NTS | NTSDDI1602XK | From the Schneider offer | 10 | Office stations, BESS yard, generator area | Terminal block | EtherNet/IP | EtherNet/IP | PRS, PMS, YRD, GEN | President 3, Prime Minister 3, yard 2, generators 2.
D35 | I/O | Edge I/O digital output, 16 channels, 24 V DC, 0.5 A | Schneider Electric | Modicon Edge I/O NTS | NTSDDO1602K | From the Schneider offer | 2 | President and PM stations | Terminal block | EtherNet/IP | EtherNet/IP | PRS, PMS | 8 commands at each office station, through interposing relays.
D36 | I/O | Edge I/O analogue input, 4 x 4-20 mA | Schneider Electric | Modicon Edge I/O NTS | To select | To confirm with supplier | 1 | Generator area | Terminal block | EtherNet/IP | EtherNet/IP | GEN | DG1 and DG2 fuel levels.
D37 | I/O | Edge I/O serial master, Modbus RTU | Schneider Electric | Modicon Edge I/O NTS | NTSFMB0120K | From the Schneider offer | 2 | President and PM stations | RS485 | Modbus RTU | Modbus RTU | - | Reads the ST260E RMU relay at each office station. Add one at the generator area if the generator controllers are RS485 only.
D38 | I/O | Edge I/O terminal blocks | Schneider Electric | Modicon Edge I/O NTS | NTSXTB02030H, NTSXTB18001XH, NTSXTB18001H, NTSXTB12001H | From the Schneider offer | 22 | Office stations, BESS yard, generator area | - | - | N/A | - | 8 power supply, 10 input, 2 output and 2 serial master blocks.
D39 | I/O | Interposing relay with base, 24 V DC coil, contact rated for the 110 V DC control circuit | Schneider Electric | Zelio Relay | To select | To confirm with supplier | 32 | Switchroom and office stations | Terminal | Hardwired | Hardwired | SWR, PRS, PMS | 30 command relays and 2 for the beacon and watchdog. Relay numbers IR01 to IR32 are on the IO List.
C. Network, time and security
D40 | Network | Core switch, managed, with SFP fibre ports | Schneider Electric | Modicon managed switch | To select | To confirm with supplier | 2 | 11 kV switchroom | RJ45 + SFP | Ethernet, VLANs, ring | N/A | - | Core switch A and B. The offer quotes MCSESM083F23F1, which has copper ports only.
D41 | Network | Field and station switch, managed, with SFP fibre ports | Schneider Electric | Modicon managed switch | To select | To confirm with supplier | 5 | MV station, BESS, generators, 2 office stations | RJ45 + SFP | Ethernet, ring | N/A | - | Replaces the unmanaged switch on the existing sheet.
D42 | Network | Fibre transceiver, single-mode | Schneider Electric | SFP for the switches above | To select | To confirm with supplier | 14 | All switches | LC fibre | - | N/A | - | 7-switch ring, 2 per link.
D43 | Network | Firewall with VPN | Fortinet | FortiGate Rugged 60F | FGR-60F | From memory - confirm | 1 | 11 kV switchroom | RJ45 | VPN, off by default | N/A | - | Not in the Schneider range offered; second unit optional.
D44 | Network | GPS time server with antenna | Meinberg | LANTIME M300 | M300/GPS | From memory - confirm | 1 | 11 kV switchroom | RJ45 | NTP | NTP | - | Not in the Schneider range offered.
D45 | Network | Armoured single-mode fibre, 12 core, with patch panels | To suit | - | Length per route | TBC | 3 | Switchroom-President, switchroom-PM, President-PM | LC | - | N/A | - | Third route closes the ring. The yard and generator area islands connect through field switches 2 and 3.
D. SCADA stations, power and enclosures
D46 | SCADA | SCADA station, industrial panel PC | Schneider Electric | Industrial panel PC | HMIP67GD0F88BE7N00 | From the Schneider offer - model to confirm | 2 | Control room | RJ45 | Modbus TCP | Modbus TCP | - | Station A active, station B hot standby; each is also an operator station.
D47 | SCADA | Engineering laptop | Dell | Latitude 5430 Rugged | Configured to order | To confirm with supplier | 1 | Control room | RJ45 | - | N/A | - | Runs EcoStruxure Control Expert and the SCADA build-time licence.
D48 | SCADA | Power meter | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | From memory - confirm | 3 | LVDB President, LVDB PM, auxiliary board | RJ45 | Modbus TCP | Modbus TCP | - | The offer lists 5 x PM5320; the design keeps 3 x PM5560.
D51 | SCADA | 24 V DC power supply | Schneider Electric | Phaseo | To select | To confirm with supplier | 6 | Switchroom, office stations, BESS yard, generator area | - | - | N/A | - | Contact wetting, Edge I/O and X80 power supplies, switches. Input to suit the 110 V DC station supply where available.
D52 | SCADA | UPS for the SCADA cabinet, 3000 VA | APC (Schneider Electric) | Smart-UPS SRT 3000 | SRT3000RMXLI | From memory - confirm | 1 | Control room | RJ45 | SNMP | N/A | - | About 2 hours runtime with battery pack; size at design.
D53 | SCADA | SCADA cabinet, 800 x 2000 x 800 mm | Schneider Electric | Spacial SF | Size to suit | To confirm with supplier | 1 | 11 kV switchroom | - | - | N/A | SWR | Door contact wired to the switchroom I/O.
D54 | SCADA | Outdoor I/O panel, IP55 minimum | Schneider Electric | Thalassa PLM | Size to suit | To confirm with supplier | 4 | Office stations, BESS yard, generator area | - | - | N/A | PRS, PMS, YRD, GEN | Shaded or air-conditioned where exposed to direct sun.
D55 | SCADA | Alarm sounder and beacon | Schneider Electric | Harmony XVS | Model to select | To confirm with supplier | 1 | Control room | Terminal | Hardwired | Hardwired | SWR
E. Software
D56 | Software | SCADA runtime, 4K tags | Schneider Electric | EcoStruxure Machine SCADA Expert | HMIEMSE3PRT4KA | From the Schneider offer | 2 | SCADA stations | - | Modbus TCP | N/A | - | One per station; about 707 tags. Operator and Admin roles. Redundancy, historian and retention to be confirmed by Schneider.
D57 | Software | SCADA build-time licence, 4K tags | Schneider Electric | EcoStruxure Machine SCADA Expert | HMIEMSEBT4KA | From the Schneider offer | 1 | Engineering laptop | - | - | N/A | -
D58 | Software | Controller engineering software | Schneider Electric | EcoStruxure Control Expert | By quotation | To confirm with supplier | 1 | Engineering laptop | - | - | N/A | - | Includes the hot standby configuration.
D59 | Software | VPN client | Fortinet | FortiClient | - | - | 1 | Remote users | - | - | N/A | -

## Protocol Summary
Primary protocol | Where used | Device lines | Device quantity
Modbus TCP | Controllers to SCADA stations; 11 kV relays, PLC box, EMS, battery via EMS, generator controllers, power meters, weather logger, UPS
EtherNet/IP | Controllers to the Edge I/O islands at the office stations, BESS yard and generator area
M580 Ethernet remote I/O | Controllers to the switchroom remote drop and its X80 modules
Modbus RTU | ST260E RMU relays through the Edge I/O serial masters; RS485 devices in the switchroom
Hardwired | Status contacts, alarms and commands wired to the I/O; commands through interposing relays
Power line communication | PV inverters to the PLC box over the AC cables
NTP | Time synchronisation from the GPS time server
Through logger | Weather sensors to the blue'Log
Supervision protocols: SNMP v3 and syslog from switches, firewall and time server to the SCADA stations. The controllers and the SCADA exchange data by Modbus TCP (EtherNet/IP is an alternative).

## IO List
Tag | Description | Equipment | Location | Type | I/O location | Module | Module reference | Channel | Normal state / range | Alarm level | Operated by | Notes
AH1-CB-OPEN | Circuit breaker open | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 1 | Status | Status | -
AH1-CB-CLSD | Circuit breaker closed | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 2 | Status | Status | -
AH1-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 3 | Normally open | 1 | -
AH1-ES-CLSD | Earth switch closed | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 4 | Status | Status | - | Interlock: blocks remote close
AH1-LR-REM | Local/remote switch in remote | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 5 | Status | Status | - | Interlock: remote commands only in remote
AH1-SPR-CHG | Closing spring charged | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 6 | Normally closed | 3 | -
AH1-GAS-LOW | Gas pressure low | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 7 | Normally open | 2 | -
AH1-RLY-OK | Protection relay healthy | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 8 | Normally closed | 2 | -
AH1-AUX-OK | Control supply healthy | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 9 | Normally closed | 2 | -
AH2-CB-OPEN | Circuit breaker open | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 10 | Status | Status | -
AH2-CB-CLSD | Circuit breaker closed | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 11 | Status | Status | -
AH2-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 12 | Normally open | 1 | -
AH2-ES-CLSD | Earth switch closed | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 13 | Status | Status | - | Interlock: blocks remote close
AH2-LR-REM | Local/remote switch in remote | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 14 | Status | Status | - | Interlock: remote commands only in remote
AH2-SPR-CHG | Closing spring charged | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 15 | Normally closed | 3 | -
AH2-GAS-LOW | Gas pressure low | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 16 | Normally open | 2 | -
AH2-RLY-OK | Protection relay healthy | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 17 | Normally closed | 2 | -
AH2-AUX-OK | Control supply healthy | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 18 | Normally closed | 2 | -
AH3-CB-OPEN | Circuit breaker open | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 19 | Status | Status | -
AH3-CB-CLSD | Circuit breaker closed | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 20 | Status | Status | -
AH3-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 21 | Normally open | 1 | -
AH3-ES-CLSD | Earth switch closed | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 22 | Status | Status | - | Interlock: blocks remote close
AH3-LR-REM | Local/remote switch in remote | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 23 | Status | Status | - | Interlock: remote commands only in remote
AH3-SPR-CHG | Closing spring charged | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI1 | BMXDDI3202K | 24 | Normally closed | 3 | -
AH3-GAS-LOW | Gas pressure low | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 1 | Normally open | 2 | -
AH3-RLY-OK | Protection relay healthy | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 2 | Normally closed | 2 | -
AH3-AUX-OK | Control supply healthy | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 3 | Normally closed | 2 | -
AH4-CB-OPEN | Circuit breaker open | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 4 | Status | Status | -
AH4-CB-CLSD | Circuit breaker closed | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 5 | Status | Status | -
AH4-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 6 | Normally open | 1 | -
AH4-ES-CLSD | Earth switch closed | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 7 | Status | Status | - | Interlock: blocks remote close
AH4-LR-REM | Local/remote switch in remote | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 8 | Status | Status | - | Interlock: remote commands only in remote
AH4-SPR-CHG | Closing spring charged | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 9 | Normally closed | 3 | -
AH4-GAS-LOW | Gas pressure low | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 10 | Normally open | 2 | -
AH4-RLY-OK | Protection relay healthy | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 11 | Normally closed | 2 | -
AH4-AUX-OK | Control supply healthy | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 12 | Normally closed | 2 | -
AH5-CB-OPEN | Circuit breaker open | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 13 | Status | Status | -
AH5-CB-CLSD | Circuit breaker closed | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 14 | Status | Status | -
AH5-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 15 | Normally open | 1 | -
AH5-ES-CLSD | Earth switch closed | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 16 | Status | Status | - | Interlock: blocks remote close
AH5-LR-REM | Local/remote switch in remote | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 17 | Status | Status | - | Interlock: remote commands only in remote
AH5-SPR-CHG | Closing spring charged | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 18 | Normally closed | 3 | -
AH5-GAS-LOW | Gas pressure low | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 19 | Normally open | 2 | -
AH5-RLY-OK | Protection relay healthy | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 20 | Normally closed | 2 | -
AH5-AUX-OK | Control supply healthy | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 21 | Normally closed | 2 | -
AH6-CB-OPEN | Circuit breaker open | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 22 | Status | Status | -
AH6-CB-CLSD | Circuit breaker closed | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 23 | Status | Status | -
AH6-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI2 | BMXDDI3202K | 24 | Normally open | 1 | -
AH6-ES-CLSD | Earth switch closed | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 1 | Status | Status | - | Interlock: blocks remote close
AH6-LR-REM | Local/remote switch in remote | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 2 | Status | Status | - | Interlock: remote commands only in remote
AH6-SPR-CHG | Closing spring charged | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 3 | Normally closed | 3 | -
AH6-GAS-LOW | Gas pressure low | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 4 | Normally open | 2 | -
AH6-RLY-OK | Protection relay healthy | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 5 | Normally closed | 2 | -
AH6-AUX-OK | Control supply healthy | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 6 | Normally closed | 2 | -
AH7-CB-OPEN | Circuit breaker open | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 7 | Status | Status | -
AH7-CB-CLSD | Circuit breaker closed | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 8 | Status | Status | -
AH7-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 9 | Normally open | 1 | -
AH7-ES-CLSD | Earth switch closed | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 10 | Status | Status | - | Interlock: blocks remote close
AH7-LR-REM | Local/remote switch in remote | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 11 | Status | Status | - | Interlock: remote commands only in remote
AH7-SPR-CHG | Closing spring charged | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 12 | Normally closed | 3 | -
AH7-GAS-LOW | Gas pressure low | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 13 | Normally open | 2 | -
AH7-RLY-OK | Protection relay healthy | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 14 | Normally closed | 2 | -
AH7-AUX-OK | Control supply healthy | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 15 | Normally closed | 2 | -
AH1-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 1 | Pulse | - | Operator | Select then confirm. Via interposing relay IR01.
AH1-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR02.
AH2-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH2, PV incomer | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 3 | Pulse | - | Operator | Select then confirm. Via interposing relay IR03.
AH2-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH2, PV incomer | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR04.
AH3-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 5 | Pulse | - | Operator | Select then confirm. Via interposing relay IR05.
AH3-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR06.
AH4-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH4, President feeder | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 7 | Pulse | - | Operator | Select then confirm. Via interposing relay IR07.
AH4-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH4, President feeder | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 8 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR08.
AH5-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 9 | Pulse | - | Operator | Select then confirm. Via interposing relay IR09.
AH5-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 10 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR10.
AH6-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 11 | Pulse | - | Operator | Select then confirm. Via interposing relay IR11.
AH6-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 12 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR12.
AH7-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 13 | Pulse | - | Operator | Select then confirm. Via interposing relay IR13.
AH7-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 14 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR14.
AH8-NER-EF | Earth fault current alarm | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 16 | Normally open | 1 | -
AH8-NER-TEMP | Resistor temperature high | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 17 | Normally open | 2 | -
AH8-AUX-OK | Panel supply healthy | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 18 | Normally closed | 2 | -
AH8-CB-OPEN | Circuit breaker open | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 19 | Status | Status | - | Added rev 1. The 11 kV system is earthed only through AH8
AH8-CB-CLSD | Circuit breaker closed | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 20 | Status | Status | - | Added rev 1. Level 1 alarm if open while the busbar is live
AH8-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 21 | Normally open | 1 | - | Added rev 1
AH8-ES-CLSD | Earth switch closed | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 22 | Status | Status | - | Added rev 1
AH8-GAS-LOW | Gas pressure low | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | SWR | SWR-DI3 | BMXDDI3202K | 23 | Normally open | 2 | - | Added rev 1
SYS-BEACON | Critical alarm beacon and sounder | Control room alarm beacon | Control room | DO | SWR | SWR-DO1 | BMXDDO3202K | 17 | De-energised | - | Automatic | Via interposing relay IR15.
SYS-CP-HEALTHY | Controller healthy output (watchdog) | Modicon M580 controllers | 11 kV switchroom | DO | SWR | SWR-DO1 | BMXDDO3202K | 18 | Energised | - | Automatic | Via interposing relay IR16.
T-AUX-OT-ALM | Oil temperature alarm | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 1 | Normally open | 3 | -
T-AUX-OT-TRIP | Oil temperature trip | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 2 | Normally open | 1 | -
T-AUX-WT-ALM | Winding temperature alarm | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 3 | Normally open | 3 | -
T-AUX-WT-TRIP | Winding temperature trip | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 4 | Normally open | 1 | -
T-AUX-PRD | Pressure relief device operated | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 5 | Normally open | 1 | -
T-AUX-OL-LOW | Oil level low | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 6 | Normally open | 2 | -
T-AUX-FUSE | HV fuse blown (XRNT-3A striker) | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 7 | Normally open | 1 | - | Added rev 1. The fuse is the only HV protection of this transformer
T-INV-OT-ALM | Oil temperature alarm | Inverter transformer | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 1 | Normally open | 3 | -
T-INV-OT-TRIP | Oil temperature trip | Inverter transformer | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 2 | Normally open | 1 | -
T-INV-WT-ALM | Winding temperature alarm | Inverter transformer | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 3 | Normally open | 3 | -
T-INV-WT-TRIP | Winding temperature trip | Inverter transformer | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 4 | Normally open | 1 | -
T-INV-PRD | Pressure relief device operated | Inverter transformer | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 5 | Normally open | 1 | -
T-INV-OL-LOW | Oil level low | Inverter transformer | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 6 | Normally open | 2 | -
PV-ACB-CLSD | PV main LV breaker (ACB 1250 A) closed | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 7 | Status | Status | - | Added rev 1
PV-ACB-TRIP | PV main LV breaker (ACB 1250 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 8 | Normally open | 1 | - | Added rev 1
NB01-MCCB-TRIP | Inverter NB01 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 9 | Normally open | 2 | - | Added rev 1
NB02-MCCB-TRIP | Inverter NB02 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 10 | Normally open | 2 | - | Added rev 1
NB03-MCCB-TRIP | Inverter NB03 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 11 | Normally open | 2 | - | Added rev 1
NB04-MCCB-TRIP | Inverter NB04 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 12 | Normally open | 2 | - | Added rev 1
BESS-ACB-CLSD | Battery main LV breaker (ACB 1000 A) closed | BESS LV breaker 0.69 kV | BESS and inverter transformer yard | DI | YRD | YRD-DI1 | NTSDDI1602XK | 13 | Status | Status | - | Added rev 1
BESS-ACB-TRIP | Battery main LV breaker (ACB 1000 A) tripped | BESS LV breaker 0.69 kV | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 1 | Normally open | 1 | - | Added rev 1
T-DG-OT-ALM | Oil temperature alarm | Generator step-up transformer | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 1 | Normally open | 3 | -
T-DG-OT-TRIP | Oil temperature trip | Generator step-up transformer | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 2 | Normally open | 1 | -
T-DG-WT-ALM | Winding temperature alarm | Generator step-up transformer | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 3 | Normally open | 3 | -
T-DG-WT-TRIP | Winding temperature trip | Generator step-up transformer | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 4 | Normally open | 1 | -
T-DG-PRD | Pressure relief device operated | Generator step-up transformer | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 5 | Normally open | 1 | -
T-DG-OL-LOW | Oil level low | Generator step-up transformer | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 6 | Normally open | 2 | -
GEN-ACB-CLSD | DG step-up transformer LV breaker closed | Generator step-up transformer | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 7 | Status | Status | - | Added rev 1
GEN-ACB-TRIP | DG step-up transformer LV breaker tripped | Generator step-up transformer | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 8 | Normally open | 1 | - | Added rev 1
DG1-GCB-CLSD | Generator breaker closed | Diesel generator DG1 | Generator area | DI | GEN | GEN-DI1 | NTSDDI1602XK | 9 | Status | Status | - | Backup to Modbus status
DG1-COM-ALM | Common alarm | Diesel generator DG1 | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 1 | Normally open | 2 | -
DG1-ESTOP | Emergency stop active | Diesel generator DG1 | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 2 | Normally open | 1 | -
DG1-RUN | Engine running | Diesel generator DG1 | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 3 | Status | Status | -
DG2-GCB-CLSD | Generator breaker closed | Diesel generator DG2 | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 4 | Status | Status | - | Backup to Modbus status
DG2-COM-ALM | Common alarm | Diesel generator DG2 | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 5 | Normally open | 2 | -
DG2-ESTOP | Emergency stop active | Diesel generator DG2 | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 6 | Normally open | 1 | -
DG2-RUN | Engine running | Diesel generator DG2 | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 7 | Status | Status | -
FIRE-PREALM | Pre-alarm | Fire detection and suppression panel | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 2 | Normally open | 2 | - | Reset at panel only
FIRE-ALM | Fire alarm | Fire detection and suppression panel | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 3 | Normally open | 1 | - | Reset at panel only
FIRE-FLT | System fault | Fire detection and suppression panel | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 4 | Normally open | 2 | - | Reset at panel only
FIRE-REL | Suppression released | Fire detection and suppression panel | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 5 | Normally open | 1 | - | Reset at panel only
FIRE-AGENT-LOW | Agent pressure low | Fire detection and suppression panel | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 6 | Normally open | 2 | - | Reset at panel only
FIRE-ISOL | System isolated | Fire detection and suppression panel | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 7 | Normally open | 2 | - | Reset at panel only
FIRE-MAN-REL | Manual release activated | Fire detection and suppression panel | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 8 | Normally open | 1 | - | Reset at panel only
FIRE-PSU-FLT | Panel supply fault | Fire detection and suppression panel | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 9 | Normally open | 2 | - | Reset at panel only
AUXLV-INC-CLSD | Auxiliary LV incomer closed | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 8 | Status | Status | -
AUXLV-INC-TRIP | Auxiliary LV incomer tripped | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 9 | Normally open | 2 | -
AUXLV-SPD-FLT | Surge arrester failed | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 10 | Normally open | 3 | -
UPS-ON-BATT | UPS on battery | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 11 | Normally open | 2 | -
UPS-BATT-LOW | UPS battery low | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 12 | Normally open | 1 | -
UPS-FLT | UPS fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 13 | Normally open | 2 | -
UPS-BYPASS | UPS on bypass | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 14 | Normally open | 3 | -
DC-CHG-FLT | DC charger fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 15 | Normally open | 2 | -
DC-EARTH-FLT | DC earth fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 16 | Normally open | 2 | -
DC-UV | DC bus undervoltage | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 17 | Normally open | 1 | -
SWR-HVAC-FLT | Switchroom air conditioning fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 18 | Normally open | 3 | -
SWR-TEMP-HI | Switchroom temperature high | Auxiliary supplies and UPS | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 19 | Normally open | 3 | -
ESTOP-SWR | Plant emergency stop pressed, switchroom | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 20 | Normally open | 1 | -
DOOR-SCADA | SCADA cabinet door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 21 | Normally open | 3 | -
DOOR-SWR | Switchroom door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 22 | Normally open | 3 | -
DOOR-GIS | 11 kV switchgear room door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | SWR | SWR-DI4 | BMXDDI3202K | 23 | Normally open | 3 | -
ESTOP-BESS | Plant emergency stop pressed, BESS area | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 10 | Normally open | 1 | -
DOOR-BESS | BESS container door open | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 11 | Normally open | 3 | -
YARD-PNL-SUP-OK | Yard I/O panel supply healthy | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 12 | Normally closed | 2 | -
YARD-PNL-DOOR | Yard I/O panel door open | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | YRD | YRD-DI2 | NTSDDI1602XK | 13 | Normally open | 3 | -
GEN-PNL-SUP-OK | Generator I/O panel supply healthy | Emergency stops, doors and I/O panels | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 8 | Normally closed | 2 | -
GEN-PNL-DOOR | Generator I/O panel door open | Emergency stops, doors and I/O panels | Generator area | DI | GEN | GEN-DI2 | NTSDDI1602XK | 9 | Normally open | 3 | -
DG1-FUEL | Fuel tank level | Diesel generator DG1 | Generator area | AI | GEN | GEN-AI1 | NTS analogue input (to select) | 1 | 4-20 mA = 0-100 % | 3 below 20 % | -
DG2-FUEL | Fuel tank level | Diesel generator DG2 | Generator area | AI | GEN | GEN-AI1 | NTS analogue input (to select) | 2 | 4-20 mA = 0-100 % | 3 below 20 % | -
DC-110-V | 110 V DC bus voltage | Auxiliary supplies and UPS | 11 kV switchroom | AI | SWR | SWR-AI1 | BMXAMI0410 | 1 | 4-20 mA = 0-150 V | 2 outside limits | -
DC-24-V | 24 V DC bus voltage | Auxiliary supplies and UPS | 11 kV switchroom | AI | SWR | SWR-AI1 | BMXAMI0410 | 2 | 4-20 mA = 0-36 V | 2 outside limits | -
PRS-RS1-OPEN | Ring switch 1 open | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 1 | Status | Status | -
PRS-RS1-CLSD | Ring switch 1 closed | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 2 | Status | Status | -
PRS-RS1-ES | Ring switch 1 earth switch closed | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 3 | Status | Status | -
PRS-RS2-OPEN | Ring switch 2 open | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 4 | Status | Status | -
PRS-RS2-CLSD | Ring switch 2 closed | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 5 | Status | Status | -
PRS-RS2-ES | Ring switch 2 earth switch closed | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 6 | Status | Status | -
PRS-CB-OPEN | Transformer breaker open | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 7 | Status | Status | -
PRS-CB-CLSD | Transformer breaker closed | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 8 | Status | Status | -
PRS-CB-ES | Transformer breaker earth switch closed | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 9 | Status | Status | -
PRS-CB-TRIP | Transformer breaker tripped by ST260E | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 10 | Normally open | 1 | -
PRS-GAS-LOW | RMU gas pressure low | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 11 | Normally open | 2 | -
PRS-LR-REM | RMU local/remote in remote | President station RMU | President station | DI | PRS | PRS-DI1 | NTSDDI1602XK | 12 | Status | Status | -
PRS-FPI | Fault passage indicator operated | President station RMU | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 1 | Normally open | 2 | -
PRS-TX-OT-ALM | Oil temperature alarm | President station transformer 630 kVA | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 2 | Normally open | 3 | -
PRS-TX-OT-TRIP | Oil temperature trip | President station transformer 630 kVA | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 3 | Normally open | 1 | -
PRS-TX-WT-ALM | Winding temperature alarm | President station transformer 630 kVA | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 4 | Normally open | 3 | -
PRS-TX-WT-TRIP | Winding temperature trip | President station transformer 630 kVA | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 5 | Normally open | 1 | -
PRS-TX-PRD | Pressure relief device operated | President station transformer 630 kVA | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 6 | Normally open | 1 | -
PRS-TX-OL-LOW | Oil level low | President station transformer 630 kVA | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 7 | Normally open | 2 | -
PRS-LV-INC-CLSD | LV incomer closed | President station LVDB | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 8 | Status | Status | -
PRS-LV-INC-TRIP | LV incomer tripped | President station LVDB | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 9 | Normally open | 2 | -
PRS-LV-F01-CLSD | Outgoing way 1 closed | President station LVDB | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 10 | Status | Status | -
PRS-LV-F02-CLSD | Outgoing way 2 closed | President station LVDB | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 11 | Status | Status | -
PRS-LV-F03-CLSD | Outgoing way 3 closed | President station LVDB | President station | DI | PRS | PRS-DI2 | NTSDDI1602XK | 12 | Status | Status | -
PRS-LV-F04-CLSD | Outgoing way 4 closed | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 1 | Status | Status | -
PRS-LV-F05-CLSD | Outgoing way 5 closed | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 2 | Status | Status | -
PRS-LV-F06-CLSD | Outgoing way 6 closed | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 3 | Status | Status | -
PRS-LV-F07-CLSD | Outgoing way 7 closed | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 4 | Status | Status | -
PRS-LV-F08-CLSD | Outgoing way 8 closed | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 5 | Status | Status | -
PRS-LV-F09-CLSD | Outgoing way 9 closed | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 6 | Status | Status | -
PRS-LV-F10-CLSD | Outgoing way 10 closed | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 7 | Status | Status | -
PRS-LV-SPD-FLT | Surge arrester failed | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 8 | Normally open | 3 | -
PRS-PNL-SUP-OK | I/O panel supply healthy | President station LVDB | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 9 | Normally closed | 2 | -
PRS-UPS-ON-BATT | RMU UPS 2 kVA on battery | President station RMU | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 10 | Normally open | 2 | - | Added rev 1. UPS shown on the transformer stations drawing
PRS-UPS-FLT | RMU UPS 2 kVA fault | President station RMU | President station | DI | PRS | PRS-DI3 | NTSDDI1602XK | 11 | Normally open | 2 | - | Added rev 1
PRS-RS1-OPEN-CMD | Open ring switch 1 | President station RMU | President station | DO | PRS | PRS-DO1 | NTSDDO1602K | 1 | Pulse | - | Operator | Select then confirm. Via interposing relay IR17.
PRS-RS1-CLOSE-CMD | Close ring switch 1 | President station RMU | President station | DO | PRS | PRS-DO1 | NTSDDO1602K | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR18.
PRS-RS2-OPEN-CMD | Open ring switch 2 | President station RMU | President station | DO | PRS | PRS-DO1 | NTSDDO1602K | 3 | Pulse | - | Operator | Select then confirm. Via interposing relay IR19.
PRS-RS2-CLOSE-CMD | Close ring switch 2 | President station RMU | President station | DO | PRS | PRS-DO1 | NTSDDO1602K | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR20.
PRS-CB-OPEN-CMD | Open transformer breaker | President station RMU | President station | DO | PRS | PRS-DO1 | NTSDDO1602K | 5 | Pulse | - | Operator | Select then confirm. Via interposing relay IR21.
PRS-CB-CLOSE-CMD | Close transformer breaker | President station RMU | President station | DO | PRS | PRS-DO1 | NTSDDO1602K | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR22.
PRS-LV-INC-OPEN-CMD | Open LV incomer | President station LVDB | President station | DO | PRS | PRS-DO1 | NTSDDO1602K | 7 | Pulse | - | Operator | Select then confirm. Via interposing relay IR23.
PRS-LV-INC-CLOSE-CMD | Close LV incomer | President station LVDB | President station | DO | PRS | PRS-DO1 | NTSDDO1602K | 8 | Pulse | - | Operator | Select then confirm. Via interposing relay IR24.
PMS-RS1-OPEN | Ring switch 1 open | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 1 | Status | Status | -
PMS-RS1-CLSD | Ring switch 1 closed | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 2 | Status | Status | -
PMS-RS1-ES | Ring switch 1 earth switch closed | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 3 | Status | Status | -
PMS-RS2-OPEN | Ring switch 2 open | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 4 | Status | Status | -
PMS-RS2-CLSD | Ring switch 2 closed | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 5 | Status | Status | -
PMS-RS2-ES | Ring switch 2 earth switch closed | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 6 | Status | Status | -
PMS-CB-OPEN | Transformer breaker open | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 7 | Status | Status | -
PMS-CB-CLSD | Transformer breaker closed | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 8 | Status | Status | -
PMS-CB-ES | Transformer breaker earth switch closed | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 9 | Status | Status | -
PMS-CB-TRIP | Transformer breaker tripped by ST260E | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 10 | Normally open | 1 | -
PMS-GAS-LOW | RMU gas pressure low | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 11 | Normally open | 2 | -
PMS-LR-REM | RMU local/remote in remote | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI1 | NTSDDI1602XK | 12 | Status | Status | -
PMS-FPI | Fault passage indicator operated | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 1 | Normally open | 2 | -
PMS-TX-OT-ALM | Oil temperature alarm | Prime Minister station transformer 630 kVA | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 2 | Normally open | 3 | -
PMS-TX-OT-TRIP | Oil temperature trip | Prime Minister station transformer 630 kVA | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 3 | Normally open | 1 | -
PMS-TX-WT-ALM | Winding temperature alarm | Prime Minister station transformer 630 kVA | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 4 | Normally open | 3 | -
PMS-TX-WT-TRIP | Winding temperature trip | Prime Minister station transformer 630 kVA | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 5 | Normally open | 1 | -
PMS-TX-PRD | Pressure relief device operated | Prime Minister station transformer 630 kVA | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 6 | Normally open | 1 | -
PMS-TX-OL-LOW | Oil level low | Prime Minister station transformer 630 kVA | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 7 | Normally open | 2 | -
PMS-LV-INC-CLSD | LV incomer closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 8 | Status | Status | -
PMS-LV-INC-TRIP | LV incomer tripped | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 9 | Normally open | 2 | -
PMS-LV-F01-CLSD | Outgoing way 1 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 10 | Status | Status | -
PMS-LV-F02-CLSD | Outgoing way 2 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 11 | Status | Status | -
PMS-LV-F03-CLSD | Outgoing way 3 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI2 | NTSDDI1602XK | 12 | Status | Status | -
PMS-LV-F04-CLSD | Outgoing way 4 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 1 | Status | Status | -
PMS-LV-F05-CLSD | Outgoing way 5 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 2 | Status | Status | -
PMS-LV-F06-CLSD | Outgoing way 6 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 3 | Status | Status | -
PMS-LV-F07-CLSD | Outgoing way 7 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 4 | Status | Status | -
PMS-LV-F08-CLSD | Outgoing way 8 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 5 | Status | Status | -
PMS-LV-F09-CLSD | Outgoing way 9 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 6 | Status | Status | -
PMS-LV-F10-CLSD | Outgoing way 10 closed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 7 | Status | Status | -
PMS-LV-SPD-FLT | Surge arrester failed | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 8 | Normally open | 3 | -
PMS-PNL-SUP-OK | I/O panel supply healthy | Prime Minister station LVDB | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 9 | Normally closed | 2 | -
PMS-UPS-ON-BATT | RMU UPS 2 kVA on battery | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 10 | Normally open | 2 | - | Added rev 1. UPS shown on the transformer stations drawing
PMS-UPS-FLT | RMU UPS 2 kVA fault | Prime Minister station RMU | Prime Minister station | DI | PMS | PMS-DI3 | NTSDDI1602XK | 11 | Normally open | 2 | - | Added rev 1
PMS-RS1-OPEN-CMD | Open ring switch 1 | Prime Minister station RMU | Prime Minister station | DO | PMS | PMS-DO1 | NTSDDO1602K | 1 | Pulse | - | Operator | Select then confirm. Via interposing relay IR25.
PMS-RS1-CLOSE-CMD | Close ring switch 1 | Prime Minister station RMU | Prime Minister station | DO | PMS | PMS-DO1 | NTSDDO1602K | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR26.
PMS-RS2-OPEN-CMD | Open ring switch 2 | Prime Minister station RMU | Prime Minister station | DO | PMS | PMS-DO1 | NTSDDO1602K | 3 | Pulse | - | Operator | Select then confirm. Via interposing relay IR27.
PMS-RS2-CLOSE-CMD | Close ring switch 2 | Prime Minister station RMU | Prime Minister station | DO | PMS | PMS-DO1 | NTSDDO1602K | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR28.
PMS-CB-OPEN-CMD | Open transformer breaker | Prime Minister station RMU | Prime Minister station | DO | PMS | PMS-DO1 | NTSDDO1602K | 5 | Pulse | - | Operator | Select then confirm. Via interposing relay IR29.
PMS-CB-CLOSE-CMD | Close transformer breaker | Prime Minister station RMU | Prime Minister station | DO | PMS | PMS-DO1 | NTSDDO1602K | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed. Via interposing relay IR30.
PMS-LV-INC-OPEN-CMD | Open LV incomer | Prime Minister station LVDB | Prime Minister station | DO | PMS | PMS-DO1 | NTSDDO1602K | 7 | Pulse | - | Operator | Select then confirm. Via interposing relay IR31.
PMS-LV-INC-CLOSE-CMD | Close LV incomer | Prime Minister station LVDB | Prime Minister station | DO | PMS | PMS-DO1 | NTSDDO1602K | 8 | Pulse | - | Operator | Select then confirm. Via interposing relay IR32.

## IO Summary
I/O location | Location | Module | Module reference | Channels | Used | Spare | Spare %
SWR | 11 kV switchroom | SWR-DI1 | BMXDDI3202K | 32
SWR | 11 kV switchroom | SWR-DI2 | BMXDDI3202K | 32
SWR | 11 kV switchroom | SWR-DI3 | BMXDDI3202K | 32
SWR | 11 kV switchroom | SWR-DI4 | BMXDDI3202K | 32
SWR | 11 kV switchroom | SWR-DO1 | BMXDDO3202K | 32
SWR | 11 kV switchroom | SWR-AI1 | BMXAMI0410 | 4
PRS | President office station | PRS-DI1 | NTSDDI1602XK | 16
PRS | President office station | PRS-DI2 | NTSDDI1602XK | 16
PRS | President office station | PRS-DI3 | NTSDDI1602XK | 16
PRS | President office station | PRS-DO1 | NTSDDO1602K | 16
PMS | Prime Minister office station | PMS-DI1 | NTSDDI1602XK | 16
PMS | Prime Minister office station | PMS-DI2 | NTSDDI1602XK | 16
PMS | Prime Minister office station | PMS-DI3 | NTSDDI1602XK | 16
PMS | Prime Minister office station | PMS-DO1 | NTSDDO1602K | 16
YRD | BESS and inverter transformer yard | YRD-DI1 | NTSDDI1602XK | 16
YRD | BESS and inverter transformer yard | YRD-DI2 | NTSDDI1602XK | 16
GEN | Generator area | GEN-DI1 | NTSDDI1602XK | 16
GEN | Generator area | GEN-DI2 | NTSDDI1602XK | 16
GEN | Generator area | GEN-AI1 | NTS AI (to select) | 4
Totals by module reference
Module reference | Description | Modules | Channels | Used | Spare | Spare %
BMXDDI3202K | X80 digital input, 32 channels, 24 V DC
BMXDDO3202K | X80 digital output, 32 channels, 24 V DC
BMXAMI0410 | X80 analogue input, 4 isolated channels
NTSDDI1602XK | Edge I/O NTS digital input, 16 channels, 24 V DC
NTSDDO1602K | Edge I/O NTS digital output, 16 channels, 24 V DC, 0.5 A
NTS AI (to select) | Edge I/O NTS analogue input, 4 channels
Total
Hardwired signals by type
Type | Meaning | Signals
DI | Digital input (status, alarm)
DO | Digital output (command, through an interposing relay)
AI | Analogue input (4-20 mA)
Total

## IO Locations
I/O location | Location | I/O hardware | Interface reference | Link to the controllers | Equipment wired here | I/O modules | Hardwired signals | Spare channels
SWR | 11 kV switchroom, SCADA cabinet | Modicon X80 remote drop | BMECRA31210 on BMEXBP1200 | M580 Ethernet remote I/O, copper, in the cabinet | 11 kV panels AH1 to AH8, alarm beacon, controller watchdog, auxiliary transformer and LV board, UPS, DC supplies, switchroom E-stop and doors
PRS | President office transformer station | Modicon Edge I/O NTS island | NTSNEC1200K | EtherNet/IP over the fibre ring, through the station switch | RMU, 630 kVA transformer, LVDB, RMU UPS; ST260E relay on the island serial master
PMS | Prime Minister office transformer station | Modicon Edge I/O NTS island | NTSNEC1200K | EtherNet/IP over the fibre ring, through the station switch | RMU, 630 kVA transformer, LVDB, RMU UPS; ST260E relay on the island serial master
YRD | BESS and inverter transformer yard | Modicon Edge I/O NTS island | NTSNEC1200K | EtherNet/IP over the fibre ring, through field switch 2 | Inverter transformer, PV and BESS LV breakers, inverter AC breakers, battery fire panel, BESS E-stop and door, panel supervision
GEN | Generator area | Modicon Edge I/O NTS island | NTSNEC1200K | EtherNet/IP over the fibre ring, through field switch 3 | DG1 and DG2 status and fuel level, DG step-up transformer and its LV breaker, panel supervision
Total
Both controllers of the M580 hot standby pair reach every location; only the active one reads inputs and drives outputs. No I/O sits in the CPU racks.
Field contacts are wired a short distance to the local I/O. Inputs are dry contacts wetted at 24 V DC from the panel supply; commands drive interposing relays in the 110 V DC control circuit.
Islands at the yard and generator area are in outdoor enclosures (IP55 minimum), shaded or air-conditioned where exposed to direct sun.
Further remote drops or Edge I/O islands can be added for new locations without changing the controllers.

## Comms Points
Device | Source / protocol | Point | Direction | Data type | Unit | Devices | Points each | Total points | Operated by | Notes
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Active power | Read | Measured | kW | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Reactive power | Read | Measured | kvar | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | 4 | 3 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | AC current L1, L2, L3 (3 points) | Read | Measured | A | 4 | 3 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Frequency | Read | Measured | Hz | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Power factor | Read | Measured | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC voltage | Read | Measured | V | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC current | Read | Measured | A | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC power | Read | Measured | kW | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Energy today | Read | Counter | kWh | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Energy total | Read | Counter | MWh | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Internal temperature | Read | Measured | deg C | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Insulation resistance | Read | Measured | kohm | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Operating state | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Fault code | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Alarm code | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Communication healthy | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Active power limit | Write | Setpoint | % | 4 | 1 |  | Admin | Normally set by the EMS; write only if the EMS allows
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Start / stop | Write | Command | - | 4 | 1 |  | Admin
Embedded EMS | Modbus TCP | Plant active power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Plant reactive power | Read | Measured | kvar | 1 | 1 |  | -
Embedded EMS | Modbus TCP | PV total power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | BESS power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Generator total power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Load power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Bus voltage | Read | Measured | kV | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Bus frequency | Read | Measured | Hz | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Operating mode | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS state | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS summary alarm | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Generator start request | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | PV curtailment active | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS heartbeat | Read/Write | Counter | - | 1 | 1 |  | Automatic | Link supervision
Embedded EMS | Modbus TCP | Operating mode select | Write | Command | - | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | State of charge minimum | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | State of charge maximum | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | Generator start threshold | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | Generator stop threshold | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | BESS power limit | Write | Setpoint | kW | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | BESS C-rate limit enable / disable | Write | Command | - | 1 | 1 |  | Admin | Calibration only; available only if the EMS exposes it
Embedded EMS | Modbus TCP | Fault reset, level 3 | Write | Command | - | 1 | 1 |  | Operator
Embedded EMS | Modbus TCP | Fault reset, levels 1 and 2 | Write | Command | - | 1 | 1 |  | Admin
Battery system ST3340UX | Through the EMS, Modbus TCP | State of charge | Read | Measured | % | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | State of health | Read | Measured | % | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC voltage | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC current | Read | Measured | A | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Active power | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Reactive power | Read | Measured | kvar | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell voltage maximum | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell voltage minimum | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell temperature maximum | Read | Measured | deg C | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell temperature minimum | Read | Measured | deg C | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Charge power limit | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Discharge power limit | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Energy charged total | Read | Counter | MWh | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Energy discharged total | Read | Counter | MWh | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Converter state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery management state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Racks online | Read | Measured | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC contactors closed | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cooling system state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 1 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 2 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 3 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Container fire status | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery combiner panel DC switch closed (2 points) | Read | Status | - | 1 | 2 |  | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery combiner panel fuse blown (2 points) | Read | Status | - | 1 | 2 |  | - | Added rev 1. As above
Generator controller DG1, DG2 | Modbus TCP or RTU | Voltage L1, L2, L3 (3 points) | Read | Measured | V | 2 | 3 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Current L1, L2, L3 (3 points) | Read | Measured | A | 2 | 3 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Active power | Read | Measured | kW | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Reactive power | Read | Measured | kvar | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Power factor | Read | Measured | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Frequency | Read | Measured | Hz | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Oil pressure | Read | Measured | kPa | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Coolant temperature | Read | Measured | deg C | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Starter battery voltage | Read | Measured | V | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Fuel level | Read | Measured | % | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Running hours | Read | Counter | h | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Number of starts | Read | Counter | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Energy total | Read | Counter | MWh | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Controller mode | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Breaker status | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Warning | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Shutdown alarm | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Start | Write | Command | - | 2 | 1 |  | Operator | Only in manual mode
Generator controller DG1, DG2 | Modbus TCP or RTU | Stop | Write | Command | - | 2 | 1 |  | Operator | Only in manual mode
Generator controller DG1, DG2 | Modbus TCP or RTU | Mode auto / manual | Write | Command | - | 2 | 1 |  | Admin
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Phase current L1, L2, L3 (3 points) | Read | Measured | A | 7 | 3 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Earth current | Read | Measured | A | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | 7 | 3 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Active power | Read | Measured | kW | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Reactive power | Read | Measured | kvar | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Power factor | Read | Measured | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Frequency | Read | Measured | Hz | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Energy import | Read | Counter | MWh | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Energy export | Read | Counter | MWh | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Breaker position | Read | Double point | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Overcurrent trip (50/51) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Earth fault trip (50N/51N) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Under / overvoltage trip (27/59) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Frequency trip (81) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Relay healthy | Read | Status | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Disturbance record available | Read | Status | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Trip circuit supervision alarm | Read | Status | - | 7 | 1 |  | - | Added rev 1
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Sensitive earth fault trip (51G) | Read | Event | - | 6 | 1 |  | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Reverse power trip (32), AH1 generator incomer | Read | Event | - | 1 | 1 |  | - | Added rev 1. Protects the generators against reverse power from PV and battery
RMU relay ST260E | Modbus RTU through the Edge I/O serial master | Phase current L1, L2, L3 (3 points) | Read | Measured | A | 2 | 3 |  | -
RMU relay ST260E | Modbus RTU through the Edge I/O serial master | Earth current | Read | Measured | A | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through the Edge I/O serial master | Breaker position | Read | Double point | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through the Edge I/O serial master | Overcurrent trip | Read | Event | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through the Edge I/O serial master | Earth fault trip | Read | Event | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through the Edge I/O serial master | Relay healthy | Read | Status | - | 2 | 1 |  | -
Power meter PM5560 | Modbus TCP | Voltage L-N, 3 phases (3 points) | Read | Measured | V | 3 | 3 |  | -
Power meter PM5560 | Modbus TCP | Current, 3 phases (3 points) | Read | Measured | A | 3 | 3 |  | -
Power meter PM5560 | Modbus TCP | Active power | Read | Measured | kW | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Reactive power | Read | Measured | kvar | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Apparent power | Read | Measured | kVA | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Power factor | Read | Measured | - | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Frequency | Read | Measured | Hz | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Active energy | Read | Counter | kWh | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Reactive energy | Read | Counter | kvarh | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Voltage THD | Read | Measured | % | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Current THD | Read | Measured | % | 3 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Plane-of-array irradiance | Read | Measured | W/m2 | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Wind speed | Read | Measured | m/s | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Wind direction | Read | Measured | deg | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Ambient temperature | Read | Measured | deg C | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Module temperature | Read | Measured | deg C | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Logger healthy | Read | Status | - | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Input voltage | Read | Measured | V | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Output load | Read | Measured | % | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Battery charge | Read | Measured | % | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Runtime remaining | Read | Measured | min | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | On battery | Read | Status | - | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Fault | Read | Status | - | 1 | 1 |  | -
Network switches (core and field) | SNMP v3 | Device healthy | Read | Status | - | 7 | 1 |  | -
Network switches (core and field) | SNMP v3 | Ring status | Read | Status | - | 7 | 1 |  | -
Firewall and GPS time server | SNMP v3 | Device healthy | Read | Status | - | 2 | 1 |  | -
Firewall and GPS time server | SNMP v3 | Time synchronised / VPN session active | Read | Status | - | 2 | 1 |  | -
PLC box | Modbus TCP | Communication healthy per inverter (4 points) | Read | Status | - | 1 | 4 |  | -
Modicon M580 controller internal | Internal | Controller healthy (controllers A and B) | Read | Status | - | 2 | 1 |  | - | Added rev 1. One per controller of the hot standby pair
Modicon M580 controller internal | Internal | Power supply 1 healthy (controllers A and B) | Read | Status | - | 2 | 1 |  | - | Added rev 1. One per controller of the hot standby pair
Modicon M580 controller internal | Internal | Power supply 2 healthy (controllers A and B) | Read | Status | - | 2 | 1 |  | - | Added rev 1. One per controller of the hot standby pair
Modicon M580 controller internal | Internal | I/O link healthy: switchroom remote drop | Read | Status | - | 1 | 1 |  | - | Rev 2. One per I/O location
Modicon M580 controller internal | Internal | I/O link healthy: President station island | Read | Status | - | 1 | 1 |  | - | Rev 2. One per I/O location
Modicon M580 controller internal | Internal | I/O link healthy: Prime Minister station island | Read | Status | - | 1 | 1 |  | - | Rev 2. One per I/O location
Modicon M580 controller internal | Internal | I/O link healthy: BESS yard island | Read | Status | - | 1 | 1 |  | - | Rev 2. One per I/O location
Modicon M580 controller internal | Internal | I/O link healthy: generator area island | Read | Status | - | 1 | 1 |  | - | Rev 2. One per I/O location
Modicon M580 controller internal | Internal | Link to each communication device healthy (8 links) | Read | Status | - | 1 | 8 |  | -
Modicon M580 controller internal | Internal | Controller active (controllers A and B) | Read | Status | - | 2 | 1 |  | - | Added rev 1. Shows which controller is in control
Modicon M580 controller internal | Internal | Standby controller synchronised and ready | Read | Status | - | 1 | 1 |  | - | Added rev 1. Off means a failure of the active controller would not be covered
Modicon M580 controller internal | Internal | Controller switchover occurred | Read | Event | - | 1 | 1 |  | - | Added rev 1. Logged with time; resets on acknowledgement
Total
Read
Write
Typical points only. Replace each block with the vendor's point table when received.

## Comms Point List
Tag | Device | Point | Direction | Data type | Unit | Source / protocol | Alarm level | Alarm when | Operated by | Notes
NB01-P | PV inverter NB01 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB01-Q | PV inverter NB01 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB01-U-L1 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-U-L2 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-U-L3 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-I-L1 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-I-L2 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-I-L3 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-F | PV inverter NB01 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB01-PF | PV inverter NB01 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB01-U-DC | PV inverter NB01 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-I-DC | PV inverter NB01 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-P-DC | PV inverter NB01 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB01-E-DAY | PV inverter NB01 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB01-E-TOT | PV inverter NB01 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB01-T-INT | PV inverter NB01 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB01-R-ISO | PV inverter NB01 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB01-STATE | PV inverter NB01 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-FLT-CODE | PV inverter NB01 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-ALM-CODE | PV inverter NB01 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-COMM-OK | PV inverter NB01 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB01-P-LIM-SP | PV inverter NB01 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB01-START-STOP-CMD | PV inverter NB01 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB02-P | PV inverter NB02 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB02-Q | PV inverter NB02 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB02-U-L1 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-U-L2 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-U-L3 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-I-L1 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-I-L2 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-I-L3 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-F | PV inverter NB02 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB02-PF | PV inverter NB02 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB02-U-DC | PV inverter NB02 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-I-DC | PV inverter NB02 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-P-DC | PV inverter NB02 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB02-E-DAY | PV inverter NB02 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB02-E-TOT | PV inverter NB02 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB02-T-INT | PV inverter NB02 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB02-R-ISO | PV inverter NB02 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB02-STATE | PV inverter NB02 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-FLT-CODE | PV inverter NB02 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-ALM-CODE | PV inverter NB02 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-COMM-OK | PV inverter NB02 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB02-P-LIM-SP | PV inverter NB02 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB02-START-STOP-CMD | PV inverter NB02 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB03-P | PV inverter NB03 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB03-Q | PV inverter NB03 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB03-U-L1 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-U-L2 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-U-L3 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-I-L1 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-I-L2 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-I-L3 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-F | PV inverter NB03 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB03-PF | PV inverter NB03 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB03-U-DC | PV inverter NB03 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-I-DC | PV inverter NB03 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-P-DC | PV inverter NB03 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB03-E-DAY | PV inverter NB03 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB03-E-TOT | PV inverter NB03 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB03-T-INT | PV inverter NB03 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB03-R-ISO | PV inverter NB03 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB03-STATE | PV inverter NB03 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-FLT-CODE | PV inverter NB03 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-ALM-CODE | PV inverter NB03 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-COMM-OK | PV inverter NB03 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB03-P-LIM-SP | PV inverter NB03 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB03-START-STOP-CMD | PV inverter NB03 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB04-P | PV inverter NB04 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB04-Q | PV inverter NB04 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB04-U-L1 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-U-L2 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-U-L3 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-I-L1 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-I-L2 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-I-L3 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-F | PV inverter NB04 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB04-PF | PV inverter NB04 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB04-U-DC | PV inverter NB04 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-I-DC | PV inverter NB04 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-P-DC | PV inverter NB04 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB04-E-DAY | PV inverter NB04 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB04-E-TOT | PV inverter NB04 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB04-T-INT | PV inverter NB04 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB04-R-ISO | PV inverter NB04 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB04-STATE | PV inverter NB04 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-FLT-CODE | PV inverter NB04 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-ALM-CODE | PV inverter NB04 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-COMM-OK | PV inverter NB04 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB04-P-LIM-SP | PV inverter NB04 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB04-START-STOP-CMD | PV inverter NB04 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
EMS-P-PLANT | Embedded EMS | Plant active power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-Q-PLANT | Embedded EMS | Plant reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
EMS-P-PV | Embedded EMS | PV total power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-BESS | Embedded EMS | BESS power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-GEN | Embedded EMS | Generator total power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-LOAD | Embedded EMS | Load power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-U-BUS | Embedded EMS | Bus voltage | Read | Measured | kV | Modbus TCP | - | - | -
EMS-F-BUS | Embedded EMS | Bus frequency | Read | Measured | Hz | Modbus TCP | - | - | -
EMS-MODE | Embedded EMS | Operating mode | Read | Status | - | Modbus TCP | Status | - | -
EMS-STATE | Embedded EMS | EMS state | Read | Status | - | Modbus TCP | Status | - | -
EMS-ALM | Embedded EMS | EMS summary alarm | Read | Status | - | Modbus TCP | 2 | On | -
EMS-GEN-START-REQ | Embedded EMS | Generator start request | Read | Status | - | Modbus TCP | 3 | On | -
EMS-PV-CURT | Embedded EMS | PV curtailment active | Read | Status | - | Modbus TCP | 3 | On | -
EMS-HEARTBEAT | Embedded EMS | EMS heartbeat | Read/Write | Counter | - | Modbus TCP | - | - | Automatic | Link supervision
EMS-MODE-CMD | Embedded EMS | Operating mode select | Write | Command | - | Modbus TCP | - | - | Admin
EMS-SOC-MIN-SP | Embedded EMS | State of charge minimum | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-SOC-MAX-SP | Embedded EMS | State of charge maximum | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-GEN-START-SP | Embedded EMS | Generator start threshold | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-GEN-STOP-SP | Embedded EMS | Generator stop threshold | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-P-BESS-LIM-SP | Embedded EMS | BESS power limit | Write | Setpoint | kW | Modbus TCP | - | - | Admin
EMS-CRATE-CMD | Embedded EMS | BESS C-rate limit enable / disable | Write | Command | - | Modbus TCP | - | - | Admin | Calibration only; available only if the EMS exposes it
EMS-RESET-L3-CMD | Embedded EMS | Fault reset, level 3 | Write | Command | - | Modbus TCP | - | - | Operator
EMS-RESET-L12-CMD | Embedded EMS | Fault reset, levels 1 and 2 | Write | Command | - | Modbus TCP | - | - | Admin
BESS-SOC | Battery system ST3340UX | State of charge | Read | Measured | % | Through the EMS, Modbus TCP | - | - | -
BESS-SOH | Battery system ST3340UX | State of health | Read | Measured | % | Through the EMS, Modbus TCP | - | - | -
BESS-U-DC | Battery system ST3340UX | DC voltage | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-I-DC | Battery system ST3340UX | DC current | Read | Measured | A | Through the EMS, Modbus TCP | - | - | -
BESS-P | Battery system ST3340UX | Active power | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-Q | Battery system ST3340UX | Reactive power | Read | Measured | kvar | Through the EMS, Modbus TCP | - | - | -
BESS-U-CELL-MAX | Battery system ST3340UX | Cell voltage maximum | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-U-CELL-MIN | Battery system ST3340UX | Cell voltage minimum | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-T-CELL-MAX | Battery system ST3340UX | Cell temperature maximum | Read | Measured | deg C | Through the EMS, Modbus TCP | - | - | -
BESS-T-CELL-MIN | Battery system ST3340UX | Cell temperature minimum | Read | Measured | deg C | Through the EMS, Modbus TCP | - | - | -
BESS-P-CHG-LIM | Battery system ST3340UX | Charge power limit | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-P-DIS-LIM | Battery system ST3340UX | Discharge power limit | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-E-CHG | Battery system ST3340UX | Energy charged total | Read | Counter | MWh | Through the EMS, Modbus TCP | - | - | -
BESS-E-DIS | Battery system ST3340UX | Energy discharged total | Read | Counter | MWh | Through the EMS, Modbus TCP | - | - | -
BESS-PCS-STATE | Battery system ST3340UX | Converter state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-BMS-STATE | Battery system ST3340UX | Battery management state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-RACKS-ON | Battery system ST3340UX | Racks online | Read | Measured | - | Through the EMS, Modbus TCP | - | - | -
BESS-DC-CONT | Battery system ST3340UX | DC contactors closed | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-COOL-STATE | Battery system ST3340UX | Cooling system state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-ALM-L1 | Battery system ST3340UX | Alarm level 1 | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | -
BESS-ALM-L2 | Battery system ST3340UX | Alarm level 2 | Read | Status | - | Through the EMS, Modbus TCP | 2 | On | -
BESS-ALM-L3 | Battery system ST3340UX | Alarm level 3 | Read | Status | - | Through the EMS, Modbus TCP | 3 | On | -
BESS-FIRE | Battery system ST3340UX | Container fire status | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | -
BESS-BCP1-SW-CLSD | Battery system ST3340UX | Battery combiner panel DC switch closed (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 2 | Off | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
BESS-BCP2-SW-CLSD | Battery system ST3340UX | Battery combiner panel DC switch closed (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 2 | Off | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
BESS-BCP1-FUSE | Battery system ST3340UX | Battery combiner panel fuse blown (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | - | Added rev 1. As above
BESS-BCP2-FUSE | Battery system ST3340UX | Battery combiner panel fuse blown (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | - | Added rev 1. As above
DG1-U-L1 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-U-L2 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-U-L3 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-I-L1 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-I-L2 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-I-L3 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-P | Generator controller DG1 | Active power | Read | Measured | kW | Modbus TCP or RTU | - | - | -
DG1-Q | Generator controller DG1 | Reactive power | Read | Measured | kvar | Modbus TCP or RTU | - | - | -
DG1-PF | Generator controller DG1 | Power factor | Read | Measured | - | Modbus TCP or RTU | - | - | -
DG1-F | Generator controller DG1 | Frequency | Read | Measured | Hz | Modbus TCP or RTU | - | - | -
DG1-OIL-P | Generator controller DG1 | Oil pressure | Read | Measured | kPa | Modbus TCP or RTU | - | - | -
DG1-COOL-T | Generator controller DG1 | Coolant temperature | Read | Measured | deg C | Modbus TCP or RTU | - | - | -
DG1-BATT-U | Generator controller DG1 | Starter battery voltage | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-FUEL-COM | Generator controller DG1 | Fuel level | Read | Measured | % | Modbus TCP or RTU | - | - | - | Communicated copy of hardwired signal DG1-FUEL
DG1-HOURS | Generator controller DG1 | Running hours | Read | Counter | h | Modbus TCP or RTU | - | - | -
DG1-STARTS | Generator controller DG1 | Number of starts | Read | Counter | - | Modbus TCP or RTU | - | - | -
DG1-E-TOT | Generator controller DG1 | Energy total | Read | Counter | MWh | Modbus TCP or RTU | - | - | -
DG1-MODE | Generator controller DG1 | Controller mode | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG1-GCB | Generator controller DG1 | Breaker status | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG1-WARN | Generator controller DG1 | Warning | Read | Status | - | Modbus TCP or RTU | 3 | On | -
DG1-SHUTDOWN | Generator controller DG1 | Shutdown alarm | Read | Status | - | Modbus TCP or RTU | 1 | On | -
DG1-START-CMD | Generator controller DG1 | Start | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG1-STOP-CMD | Generator controller DG1 | Stop | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG1-MODE-CMD | Generator controller DG1 | Mode auto / manual | Write | Command | - | Modbus TCP or RTU | - | - | Admin
DG2-U-L1 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-U-L2 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-U-L3 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-I-L1 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-I-L2 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-I-L3 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-P | Generator controller DG2 | Active power | Read | Measured | kW | Modbus TCP or RTU | - | - | -
DG2-Q | Generator controller DG2 | Reactive power | Read | Measured | kvar | Modbus TCP or RTU | - | - | -
DG2-PF | Generator controller DG2 | Power factor | Read | Measured | - | Modbus TCP or RTU | - | - | -
DG2-F | Generator controller DG2 | Frequency | Read | Measured | Hz | Modbus TCP or RTU | - | - | -
DG2-OIL-P | Generator controller DG2 | Oil pressure | Read | Measured | kPa | Modbus TCP or RTU | - | - | -
DG2-COOL-T | Generator controller DG2 | Coolant temperature | Read | Measured | deg C | Modbus TCP or RTU | - | - | -
DG2-BATT-U | Generator controller DG2 | Starter battery voltage | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-FUEL-COM | Generator controller DG2 | Fuel level | Read | Measured | % | Modbus TCP or RTU | - | - | - | Communicated copy of hardwired signal DG2-FUEL
DG2-HOURS | Generator controller DG2 | Running hours | Read | Counter | h | Modbus TCP or RTU | - | - | -
DG2-STARTS | Generator controller DG2 | Number of starts | Read | Counter | - | Modbus TCP or RTU | - | - | -
DG2-E-TOT | Generator controller DG2 | Energy total | Read | Counter | MWh | Modbus TCP or RTU | - | - | -
DG2-MODE | Generator controller DG2 | Controller mode | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG2-GCB | Generator controller DG2 | Breaker status | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG2-WARN | Generator controller DG2 | Warning | Read | Status | - | Modbus TCP or RTU | 3 | On | -
DG2-SHUTDOWN | Generator controller DG2 | Shutdown alarm | Read | Status | - | Modbus TCP or RTU | 1 | On | -
DG2-START-CMD | Generator controller DG2 | Start | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG2-STOP-CMD | Generator controller DG2 | Stop | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG2-MODE-CMD | Generator controller DG2 | Mode auto / manual | Write | Command | - | Modbus TCP or RTU | - | - | Admin
AH1-I-L1 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-L2 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-L3 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-E | 11 kV protection relay AH1 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L1 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L2 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L3 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-P | 11 kV protection relay AH1 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH1-Q | 11 kV protection relay AH1 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH1-PF | 11 kV protection relay AH1 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH1-F | 11 kV protection relay AH1 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH1-E-IMP | 11 kV protection relay AH1 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH1-E-EXP | 11 kV protection relay AH1 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH1-CB-POS | 11 kV protection relay AH1 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH1-TRIP-50 | 11 kV protection relay AH1 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-50N | 11 kV protection relay AH1 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-27-59 | 11 kV protection relay AH1 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-81 | 11 kV protection relay AH1 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-RLY-HEALTHY | 11 kV protection relay AH1 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH1-DREC | 11 kV protection relay AH1 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH1-TCS-ALM | 11 kV protection relay AH1 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH1-TRIP-51G | 11 kV protection relay AH1 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH1-TRIP-32 | 11 kV protection relay AH1 | Reverse power trip (32), AH1 generator incomer | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Protects the generators against reverse power from PV and battery
AH2-I-L1 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-L2 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-L3 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-E | 11 kV protection relay AH2 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L1 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L2 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L3 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-P | 11 kV protection relay AH2 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH2-Q | 11 kV protection relay AH2 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH2-PF | 11 kV protection relay AH2 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH2-F | 11 kV protection relay AH2 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH2-E-IMP | 11 kV protection relay AH2 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH2-E-EXP | 11 kV protection relay AH2 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH2-CB-POS | 11 kV protection relay AH2 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH2-TRIP-50 | 11 kV protection relay AH2 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-50N | 11 kV protection relay AH2 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-27-59 | 11 kV protection relay AH2 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-81 | 11 kV protection relay AH2 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-RLY-HEALTHY | 11 kV protection relay AH2 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH2-DREC | 11 kV protection relay AH2 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH2-TCS-ALM | 11 kV protection relay AH2 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH2-TRIP-51G | 11 kV protection relay AH2 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH3-I-L1 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-L2 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-L3 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-E | 11 kV protection relay AH3 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L1 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L2 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L3 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-P | 11 kV protection relay AH3 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH3-Q | 11 kV protection relay AH3 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH3-PF | 11 kV protection relay AH3 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH3-F | 11 kV protection relay AH3 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH3-E-IMP | 11 kV protection relay AH3 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH3-E-EXP | 11 kV protection relay AH3 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH3-CB-POS | 11 kV protection relay AH3 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH3-TRIP-50 | 11 kV protection relay AH3 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-50N | 11 kV protection relay AH3 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-27-59 | 11 kV protection relay AH3 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-81 | 11 kV protection relay AH3 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-RLY-HEALTHY | 11 kV protection relay AH3 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH3-DREC | 11 kV protection relay AH3 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH3-TCS-ALM | 11 kV protection relay AH3 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH3-TRIP-51G | 11 kV protection relay AH3 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH4-I-L1 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-L2 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-L3 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-E | 11 kV protection relay AH4 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L1 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L2 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L3 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-P | 11 kV protection relay AH4 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH4-Q | 11 kV protection relay AH4 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH4-PF | 11 kV protection relay AH4 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH4-F | 11 kV protection relay AH4 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH4-E-IMP | 11 kV protection relay AH4 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH4-E-EXP | 11 kV protection relay AH4 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH4-CB-POS | 11 kV protection relay AH4 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH4-TRIP-50 | 11 kV protection relay AH4 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-50N | 11 kV protection relay AH4 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-27-59 | 11 kV protection relay AH4 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-81 | 11 kV protection relay AH4 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-RLY-HEALTHY | 11 kV protection relay AH4 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH4-DREC | 11 kV protection relay AH4 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH4-TCS-ALM | 11 kV protection relay AH4 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH4-TRIP-51G | 11 kV protection relay AH4 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH5-I-L1 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-L2 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-L3 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-E | 11 kV protection relay AH5 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L1 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L2 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L3 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-P | 11 kV protection relay AH5 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH5-Q | 11 kV protection relay AH5 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH5-PF | 11 kV protection relay AH5 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH5-F | 11 kV protection relay AH5 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH5-E-IMP | 11 kV protection relay AH5 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH5-E-EXP | 11 kV protection relay AH5 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH5-CB-POS | 11 kV protection relay AH5 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH5-TRIP-50 | 11 kV protection relay AH5 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-50N | 11 kV protection relay AH5 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-27-59 | 11 kV protection relay AH5 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-81 | 11 kV protection relay AH5 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-RLY-HEALTHY | 11 kV protection relay AH5 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH5-DREC | 11 kV protection relay AH5 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH5-TCS-ALM | 11 kV protection relay AH5 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH6-I-L1 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-L2 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-L3 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-E | 11 kV protection relay AH6 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L1 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L2 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L3 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-P | 11 kV protection relay AH6 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH6-Q | 11 kV protection relay AH6 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH6-PF | 11 kV protection relay AH6 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH6-F | 11 kV protection relay AH6 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH6-E-IMP | 11 kV protection relay AH6 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH6-E-EXP | 11 kV protection relay AH6 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH6-CB-POS | 11 kV protection relay AH6 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH6-TRIP-50 | 11 kV protection relay AH6 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-50N | 11 kV protection relay AH6 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-27-59 | 11 kV protection relay AH6 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-81 | 11 kV protection relay AH6 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-RLY-HEALTHY | 11 kV protection relay AH6 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH6-DREC | 11 kV protection relay AH6 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH6-TCS-ALM | 11 kV protection relay AH6 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH6-TRIP-51G | 11 kV protection relay AH6 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH7-I-L1 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-L2 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-L3 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-E | 11 kV protection relay AH7 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L1 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L2 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L3 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-P | 11 kV protection relay AH7 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH7-Q | 11 kV protection relay AH7 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH7-PF | 11 kV protection relay AH7 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH7-F | 11 kV protection relay AH7 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH7-E-IMP | 11 kV protection relay AH7 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH7-E-EXP | 11 kV protection relay AH7 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH7-CB-POS | 11 kV protection relay AH7 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH7-TRIP-50 | 11 kV protection relay AH7 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-50N | 11 kV protection relay AH7 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-27-59 | 11 kV protection relay AH7 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-81 | 11 kV protection relay AH7 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-RLY-HEALTHY | 11 kV protection relay AH7 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH7-DREC | 11 kV protection relay AH7 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH7-TCS-ALM | 11 kV protection relay AH7 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH7-TRIP-51G | 11 kV protection relay AH7 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
PRS-RLY-I-L1 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through the Edge I/O serial master | - | - | -
PRS-RLY-I-L2 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through the Edge I/O serial master | - | - | -
PRS-RLY-I-L3 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through the Edge I/O serial master | - | - | -
PRS-RLY-I-E | RMU relay ST260E | Earth current | Read | Measured | A | Modbus RTU through the Edge I/O serial master | - | - | -
PRS-RLY-CB-POS | RMU relay ST260E | Breaker position | Read | Double point | - | Modbus RTU through the Edge I/O serial master | Status | - | -
PRS-RLY-TRIP-50 | RMU relay ST260E | Overcurrent trip | Read | Event | - | Modbus RTU through the Edge I/O serial master | 1 | On | -
PRS-RLY-TRIP-50N | RMU relay ST260E | Earth fault trip | Read | Event | - | Modbus RTU through the Edge I/O serial master | 1 | On | -
PRS-RLY-HEALTHY | RMU relay ST260E | Relay healthy | Read | Status | - | Modbus RTU through the Edge I/O serial master | 2 | Off | -
PMS-RLY-I-L1 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through the Edge I/O serial master | - | - | -
PMS-RLY-I-L2 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through the Edge I/O serial master | - | - | -
PMS-RLY-I-L3 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through the Edge I/O serial master | - | - | -
PMS-RLY-I-E | RMU relay ST260E | Earth current | Read | Measured | A | Modbus RTU through the Edge I/O serial master | - | - | -
PMS-RLY-CB-POS | RMU relay ST260E | Breaker position | Read | Double point | - | Modbus RTU through the Edge I/O serial master | Status | - | -
PMS-RLY-TRIP-50 | RMU relay ST260E | Overcurrent trip | Read | Event | - | Modbus RTU through the Edge I/O serial master | 1 | On | -
PMS-RLY-TRIP-50N | RMU relay ST260E | Earth fault trip | Read | Event | - | Modbus RTU through the Edge I/O serial master | 1 | On | -
PMS-RLY-HEALTHY | RMU relay ST260E | Relay healthy | Read | Status | - | Modbus RTU through the Edge I/O serial master | 2 | Off | -
PRS-LV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
PRS-LV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
PRS-LV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
PRS-LV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
PRS-LV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
PRS-LV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
PRS-LV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
PRS-LV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
PRS-LV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
PMS-LV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
PMS-LV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
PMS-LV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
PMS-LV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
PMS-LV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
PMS-LV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
PMS-LV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
PMS-LV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
PMS-LV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
AUXLV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
AUXLV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
AUXLV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
AUXLV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
AUXLV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
AUXLV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
AUXLV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
AUXLV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
AUXLV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
WS-IRR-POA | Weather logger blue'Log XM | Plane-of-array irradiance | Read | Measured | W/m2 | Modbus TCP | - | - | -
WS-WIND-SPD | Weather logger blue'Log XM | Wind speed | Read | Measured | m/s | Modbus TCP | - | - | -
WS-WIND-DIR | Weather logger blue'Log XM | Wind direction | Read | Measured | deg | Modbus TCP | - | - | -
WS-T-AMB | Weather logger blue'Log XM | Ambient temperature | Read | Measured | deg C | Modbus TCP | - | - | -
WS-T-MOD | Weather logger blue'Log XM | Module temperature | Read | Measured | deg C | Modbus TCP | - | - | -
WS-HEALTHY | Weather logger blue'Log XM | Logger healthy | Read | Status | - | Modbus TCP | 2 | Off | -
UPS-U-IN | UPS | Input voltage | Read | Measured | V | Modbus TCP or SNMP | - | - | -
UPS-LOAD | UPS | Output load | Read | Measured | % | Modbus TCP or SNMP | - | - | -
UPS-BATT-CHG | UPS | Battery charge | Read | Measured | % | Modbus TCP or SNMP | - | - | -
UPS-RUNTIME | UPS | Runtime remaining | Read | Measured | min | Modbus TCP or SNMP | - | - | -
UPS-ON-BATT-COM | UPS | On battery | Read | Status | - | Modbus TCP or SNMP | 2 | On | - | Communicated copy of hardwired signal UPS-ON-BATT
UPS-FLT-COM | UPS | Fault | Read | Status | - | Modbus TCP or SNMP | 2 | On | - | Communicated copy of hardwired signal UPS-FLT
SW-CORE-A-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-A-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-B-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-B-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-MV-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-MV-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-BESS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-BESS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-GEN-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-GEN-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PRS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PRS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PMS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PMS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
FW-HEALTHY | Firewall and GPS time server | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
FW-VPN-ACTIVE | Firewall and GPS time server | Time synchronised / VPN session active | Read | Status | - | SNMP v3 | 3 | On | -
GPS-HEALTHY | Firewall and GPS time server | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
GPS-TIME-SYNC | Firewall and GPS time server | Time synchronised / VPN session active | Read | Status | - | SNMP v3 | 3 | Off | -
PLCBOX-NB01-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB02-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB03-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB04-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
CP-A-HEALTHY | Modicon M580 controller A | Controller A healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-A-PS1-OK | Modicon M580 controller A | Controller A power supply 1 healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-A-PS2-OK | Modicon M580 controller A | Controller A power supply 2 healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-A-ACTIVE | Modicon M580 controller A | Controller A active | Read | Status | - | Internal | Status | - | - | Added rev 1. Shows which controller is in control
CP-B-HEALTHY | Modicon M580 controller B | Controller B healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-B-PS1-OK | Modicon M580 controller B | Controller B power supply 1 healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-B-PS2-OK | Modicon M580 controller B | Controller B power supply 2 healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-B-ACTIVE | Modicon M580 controller B | Controller B active | Read | Status | - | Internal | Status | - | - | Added rev 1. Shows which controller is in control
CP-IO-SWR-OK | Modicon M580 controller | I/O link healthy: switchroom remote drop | Read | Status | - | Internal | 2 | Off | - | Rev 2. One per I/O location
CP-IO-PRS-OK | Modicon M580 controller | I/O link healthy: President station island | Read | Status | - | Internal | 2 | Off | - | Rev 2. One per I/O location
CP-IO-PMS-OK | Modicon M580 controller | I/O link healthy: Prime Minister station island | Read | Status | - | Internal | 2 | Off | - | Rev 2. One per I/O location
CP-IO-YRD-OK | Modicon M580 controller | I/O link healthy: BESS yard island | Read | Status | - | Internal | 2 | Off | - | Rev 2. One per I/O location
CP-IO-GEN-OK | Modicon M580 controller | I/O link healthy: generator area island | Read | Status | - | Internal | 2 | Off | - | Rev 2. One per I/O location
CP-LINK1-OK | Modicon M580 controller | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK2-OK | Modicon M580 controller | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK3-OK | Modicon M580 controller | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK4-OK | Modicon M580 controller | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK5-OK | Modicon M580 controller | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK6-OK | Modicon M580 controller | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK7-OK | Modicon M580 controller | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK8-OK | Modicon M580 controller | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-REDUN-OK | Modicon M580 controller | Standby controller synchronised and ready | Read | Status | - | Internal | 2 | Off | - | Added rev 1. Off means a failure of the active controller would not be covered
CP-SWITCHOVER | Modicon M580 controller | Controller switchover occurred | Read | Event | - | Internal | 3 | On | - | Added rev 1. Logged with time; resets on acknowledgement

## Datasheets
No. | Group | Item | Manufacturer | Model | Order no. to search | Documents to collect | Where to download | Collected
1 | Controller | Hot standby CPU | Schneider Electric | Modicon M580 | BMEH582040 | Datasheet; M580 hot standby system planning guide; cybersecurity guide | se.com: search the reference, tab 'Documents' (datasheet, user manual)
2 | Controller | Dual power supply backplane | Schneider Electric | Modicon X80 | BMEXBP0602 | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
3 | Controller | Redundant power supply | Schneider Electric | Modicon X80 | To select | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
4 | Controller | Ethernet communication modules | Schneider Electric | Modicon M580 | BMENOC0311, BMENOC0321 | Datasheet; communication modules user manual | se.com: search the reference, tab 'Documents' (datasheet, user manual)
5 | I/O | Ethernet backplane and remote drop adapter | Schneider Electric | Modicon X80 | BMEXBP1200, BMECRA31210 | Datasheet; remote I/O system planning guide | se.com: search the reference, tab 'Documents' (datasheet, user manual)
6 | I/O | Power supply | Schneider Electric | Modicon X80 | BMXCPS3020 | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
7 | I/O | Digital input and output modules | Schneider Electric | Modicon X80 | BMXDDI3202K, BMXDDO3202K, BMXFCW303 | Datasheet; discrete I/O user manual | se.com: search the reference, tab 'Documents' (datasheet, user manual)
8 | I/O | Analogue input module | Schneider Electric | Modicon X80 | BMXAMI0410 | Datasheet; analogue I/O user manual | se.com: search the reference, tab 'Documents' (datasheet, user manual)
9 | I/O | Serial link module | Schneider Electric | Modicon X80 | BMXNOM0200 | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
10 | I/O | Edge I/O network interface and power supply | Schneider Electric | Modicon Edge I/O NTS | NTSNEC1200K, NTSPFB1002HK | Datasheet; Edge I/O NTS user manual | se.com: search the reference, tab 'Documents' (datasheet, user manual)
11 | I/O | Edge I/O digital input and output | Schneider Electric | Modicon Edge I/O NTS | NTSDDI1602XK, NTSDDO1602K | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
12 | I/O | Edge I/O analogue input | Schneider Electric | Modicon Edge I/O NTS | To select | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
13 | I/O | Edge I/O serial master | Schneider Electric | Modicon Edge I/O NTS | NTSFMB0120K | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
14 | I/O | Interposing relays | Schneider Electric | Zelio Relay | To select | Datasheet incl. DC contact rating | se.com: search the reference, tab 'Documents' (datasheet, user manual)
15 | SCADA | SCADA stations | Schneider Electric | Industrial panel PC | HMIP67GD0F88BE7N00 | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
16 | Software | SCADA software | Schneider Electric | EcoStruxure Machine SCADA Expert | HMIEMSE3PRT4KA, HMIEMSEBT4KA | Product description; system requirements; redundancy and licensing | se.com: search the reference, tab 'Documents' (datasheet, user manual)
17 | Software | Controller engineering software | Schneider Electric | EcoStruxure Control Expert | By quotation | Product information; system requirements | se.com: search the reference, tab 'Documents' (datasheet, user manual)
18 | Network | Core, field and station switches with SFP ports | Schneider Electric | Modicon managed switch | To select | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
19 | Network | Fibre transceivers | Schneider Electric | SFP, single-mode | To select | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
20 | Network | Firewall and VPN | Fortinet | FortiGate Rugged 60F | FGR-60F | Datasheet | fortinet.com data sheets library
21 | Network | GPS time server | Meinberg | LANTIME M300/GPS | M300/GPS | Datasheet | meinbergglobal.com, product page LANTIME M300
22 | Power | Power meters | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | Datasheet; Modbus register list | se.com: search the reference, tab 'Documents' (datasheet, user manual)
23 | Power | 24 V DC power supplies | Schneider Electric | Phaseo | To select | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
24 | Power | UPS | APC (Schneider Electric) | Smart-UPS SRT 3000 VA | SRT3000RMXLI | Datasheet | apc.com or se.com, search 'SRT3000RMXLI'
25 | Enclosure | SCADA cabinet | Schneider Electric | Spacial SF | Size to suit | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
26 | Enclosure | Outdoor I/O panels | Schneider Electric | Thalassa PLM | Size to suit | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
27 | Enclosure | Alarm sounder and beacon | Schneider Electric | Harmony XVS | Model to select | Datasheet | se.com: search the reference, tab 'Documents' (datasheet, user manual)
28 | Field device | PV inverters | Sungrow | SG350HX | - | Datasheet; communication protocol | sungrowpower.com product page; or PV designer
29 | Field device | Power line communication box | Sungrow | TBC | - | Datasheet; Modbus point table | PV designer
30 | Field device | Battery system | Sungrow | ST3340UX | - | Datasheet; communication protocol | Battery supplier
31 | Field device | Embedded EMS | TBC | TBC | - | Datasheet; Modbus point table | PV designer
32 | Field device | Generator controllers | TBC | TBC | - | Datasheet; Modbus point table | Generator supplier
33 | Field device | 11 kV protection relays | TBC | TBC | - | Datasheet; IEC 61850 or Modbus documentation | Switchgear supplier
34 | Field device | RMU relays | Per RMU supplier | ST260E | - | Datasheet; Modbus map | RMU supplier
35 | Field device | Fire detection and suppression panel | TBC | TBC | - | Datasheet; contact schedule | Fire system supplier
36 | Field device | Weather logger | Meteocontrol | blue'Log XM | - | Datasheet; Modbus documentation | meteocontrol.com product page
37 | Field device | Pyranometer | Kipp & Zonen | SMP12-A | - | Datasheet | kippzonen.com / otthydromet.com product page
38 | Field device | Wind sensor | Gill Instruments | WindSonic RS485 | - | Datasheet | gillinstruments.com product page
Fill the Collected column as each file is saved. Name files '<No.>_<Model>.pdf' so they sort in this order inside the zip.