## Read Me
Villa Somalia Hybrid Plant: SCADA Device and I/O List
Project | Solarization of Villa Somalia, Mogadishu. 1,516 kWp PV, 3,340 kWh BESS, 2 diesel generators, 11 kV switchboard, 2 office transformer stations.
Status | Rev 1, 15 Oct 2026: harmonised with the design report, the drawings and the HMI demonstration. For client submission as Attachment B.
Controller | Two Siemens SICAM A8000 CP-8050 in hot standby (A active, B standby) as plant controller and gateway. The embedded EMS keeps dispatch of PV, battery and generators.
SCADA | Siemens SICAM SCC on two servers (active and hot standby), linked to both controllers by IEC 60870-5-104.
Sheets
Device List | Every device in the design: model, product or ordering number, quantity, location, interface and protocol to the CP-8050.
Protocol Summary | Device quantities per protocol, calculated from the Device List.
IO List | Every hardwired signal: tag, description, type, I/O row, module and channel, alarm level and who may operate it.
Datasheets | Register of every datasheet and software document for Attachment C, with where to download it and a Collected column.
IO Rows | Where each of the six I/O rows sits, its remote interface, link to the CP-8050 and the equipment wired to it.
IO Summary | Channels used and spare per I/O module, calculated from the IO List.
Comms Points | Typical signals read or written over communication links, per device type, with quantities. Replace with each vendor's point table.
Comms Point List | The Comms Points expanded to one row per signal, each with its own tag and alarm level, as used by the HMI.
Number status key
Checked | Product number found on a supplier listing or a Siemens configuration document.
From memory - confirm | Ordering code from knowledge of the maker's catalogue; not checked online. Confirm with the distributor.
To confirm with supplier | Product exists but its number was not found. Take it from the supplier's quotation.
Existing (drawings) | Device already specified in drawing set VILLA_SOMALIA_05_10_2026.
TBC | Make or model unknown. Must come from the PV designer or the equipment supplier. Cells marked TBC are shaded yellow.
Assumptions
1 | Auxiliary control voltage is 110 V DC. This selects DI-8112, CI-8532, CI-8533 and PS-8642. For 24 V or 220 V DC see the variant note on the Device List.
2 | 11 kV breakers, RMU switches and LVDB incomers are motorised and accept remote open and close.
3 | The embedded EMS offers Modbus TCP. The PV inverter data reaches the CP-8050 from the power line communication box, as shown on the existing communication sheet.
4 | Signal counts per device are typical values. They must be checked against the switchgear, RMU, transformer and fire panel terminal schedules.
5 | Measurements (current, voltage, power, energy) come over communication from relays, meters and the EMS, not hardwired.
6 | Spare capacity target is about 20% per I/O row.
7 | Field signals are collected by the nearest I/O row: switchroom (rows 1, 2), office stations (rows 3, 4), BESS and inverter transformer yard (row 5), generator area (row 6). Remote rows 3 to 6 link to the CP-8050 by fibre. Actual cable distances are not known yet.
Revision 1 changes
1 | AH8: breaker open, closed, tripped, earth switch and gas pressure added (row 1). The 11 kV system is earthed only through AH8.
2 | LV main breakers added: PV ACB 1250 A and BESS ACB 1000 A (row 5), DG step-up transformer LV ACB (row 6).
3 | Combiner panels: trip of the four inverter AC MCCBs (row 5); battery combiner panel switch and fuse status through the EMS.
4 | Auxiliary transformer XRNT-3A fuse blown (row 2); RMU UPS 2 kVA on battery and fault at both office stations (rows 3, 4).
5 | 11 kV relays: trip circuit supervision (7), sensitive earth fault trip (6) and reverse power trip on AH1 added as communication points.
6 | Totals: 244 hardwired signals and 463 communication points. Overall spare is 27%; row 5 drops to 19% (6 of 32 channels), just under the 20% target: add a third DI-8112 there if more yard signals appear.
7 | Comms Point List sheet added. Devices D49 and D50 added to the Device List.
8 | Controller made redundant: two CP-8050 (A active, B hot standby), each with two power supplies, its own Ethernet interface, flash card and licences. I/O row 1 moved off the controller backplane onto its own CI-8532 so both controllers reach it. Communication points added for each controller's health and supplies, which controller is active, standby ready and switchover. Siemens to confirm the redundancy function, switchover time and how the I/O rows connect to both controllers.

## Device List
ID | Group | Device | Manufacturer | Model | Product / ordering no. | Number status | Qty | Location | Physical interface | Protocol to CP-8050 | Primary protocol | Hardwired to I/O row | Notes
A. Plant equipment (existing or by others)
D01 | Plant | PV string inverters NB01 to NB04 | Sungrow | SG350HX | - | Existing (drawings) | 4 | PV field | AC power cable | Power line communication to the PLC box | Power line communication | - | Not connected to the CP-8050 directly.
D02 | Plant | Power line communication box (PLC box) | Sungrow | TBC | TBC | TBC | 1 | Inverter MV station | Ethernet RJ45 | Modbus TCP (to confirm) | Modbus TCP | - | Converts inverter data to Ethernet. Get model and point table from the PV designer.
D03 | Plant | Embedded energy management system (EMS) | TBC | TBC | TBC | TBC | 1 | BESS / EMS area | Ethernet RJ45 | Modbus TCP (to confirm) | Modbus TCP | - | Dispatches PV, battery and generators. Only the CP-8050 writes settings to it.
D04 | Plant | Battery energy storage system, 3,340 kWh | Sungrow | ST3340UX | - | Existing (drawings) | 1 | BESS area | Ethernet (via EMS) | Through the EMS, Modbus TCP | Modbus TCP | - | Confirm whether battery data is read through the EMS or directly. Battery combiner panel status read through the EMS if available (rev 1).
D05 | Plant | Generator controllers DG1, DG2 | TBC | TBC | TBC | TBC | 2 | Generator area | Ethernet or RS485 | Modbus TCP, or Modbus RTU through a gateway | Modbus TCP | Row 6 | Breaker status, alarm, E-stop, running and fuel level also hardwired to row 6.
D06 | Plant | 11 kV protection relays, panels AH1 to AH7 | TBC (switchgear supplier) | TBC | TBC | TBC | 7 | 11 kV switchroom | Ethernet, 2 ports preferred | IEC 61850 MMS, or Modbus TCP | IEC 61850 | Row 1 | Dual-connect to both core switches if the relay has two ports.
D07 | Plant | Neutral earthing resistor panel AH8 | TBC (switchgear supplier) | - | - | TBC | 1 | 11 kV switchroom | Dry contacts | Hardwired | Hardwired | Row 1 | Breaker position, trip, earth switch and gas pressure also wired to row 1 (rev 1).
D08 | Plant | RMU protection relays | Per RMU supplier | ST260E | - | Existing (drawings) | 2 | President and PM stations | RS485 | Modbus RTU, converted by MGate gateway | Modbus RTU | Rows 3, 4 | Confirm Modbus map with the RMU supplier.
D09 | Plant | Transformers: inverter, DG step-up, 100 kVA auxiliary | TBC | - | - | TBC | 3 | Yard, generator area, switchroom | Dry contacts | Hardwired | Hardwired | Rows 5, 6, 2 | Each wired to the nearest I/O row: inverter to row 5, DG step-up to row 6, auxiliary to row 2. Auxiliary transformer also has its XRNT-3A fuse striker wired to row 2 (rev 1).
D10 | Plant | Transformers 630 kVA, President and PM stations | TBC | - | - | TBC | 2 | Office stations | Dry contacts | Hardwired | Hardwired | Rows 3, 4
D11 | Plant | Low-voltage distribution boards, 10-way | TBC | - | - | TBC | 2 | Office stations | Dry contacts + meter | Hardwired; meter on Modbus TCP | Hardwired | Rows 3, 4
D12 | Plant | Fire detection and suppression panel | TBC | TBC | TBC | TBC | 1 | BESS area | Dry contacts | Hardwired | Hardwired | Row 5 | Also a direct hardwired trip to the battery, outside the SCADA.
D13 | Plant | UPS and auxiliary DC supplies | TBC | TBC | TBC | TBC | 1 | 11 kV switchroom | Ethernet or dry contacts | Modbus TCP or SNMP, plus contacts | Modbus TCP | Row 2
D14 | Plant | Weather station data logger | Meteocontrol | blue'Log XM with Multi I/O and Fieldbus Ext | - | Existing (drawings) | 1 | Inverter MV station | Ethernet RJ45 | Modbus TCP | Modbus TCP | - | Collects the sensors below.
D15 | Plant | Pyranometer | Kipp & Zonen | SMP12-A | - | Existing (drawings) | 1 | Weather mast | RS485 to logger | Through the blue'Log | Through logger | -
D16 | Plant | Wind sensor | Gill Instruments | WindSonic RS485 | - | Existing (drawings) | 1 | Weather mast | RS485 to logger | Through the blue'Log | Through logger | -
D17 | Plant | Ambient and module temperature sensors | TBC | - | - | Existing (drawings) | 2 | Weather mast / PV array | Analogue to logger | Through the blue'Log | Through logger | -
D49 | Plant | LV main breakers: PV ACB 1250 A, BESS ACB 1000 A, DG step-up LV ACB; inverter AC MCCBs 400 A | TBC (switchboard supplier) | - | - | Existing (drawings) | 3 | Inverter MV station, BESS area, generator area | Dry contacts | Hardwired | Hardwired | Rows 5, 6 | Added rev 1. Position and trip of each main breaker; trip of the four inverter MCCBs (row 5).
D50 | Plant | RMU UPS 2 kVA, 220 V AC | TBC (RMU supplier) | - | - | Existing (drawings) | 2 | President and PM stations | Dry contacts | Hardwired | Hardwired | Rows 3, 4 | Added rev 1. On battery and fault contacts.
B. SICAM A8000 controller and I/O
D18 | Controller | Processor module | Siemens | CP-8050 | 6MF2805-0AA00 | Checked | 2 | 11 kV switchroom, SCADA cabinet | 2 x RJ45 | Gateway for all protocols | IEC 60870-5-104 | - | Hot standby pair (rev 1): controller A active, controller B standby, both on both core switches. Both connect to the SCADA servers by IEC 104. Siemens to confirm the redundancy function, switchover time and how the I/O rows connect to both controllers.
D19 | Controller | Power supply, 100 to 240 V DC/AC, 45 W | Siemens | PS-8642 | 6MF2864-2AA00 | Checked | 4 | 11 kV switchroom | - | - | N/A | - | Two per controller (rev 1). Confirm the CP-8050 supports a second supply.
D20 | Controller | Ethernet interface, 5 x RJ45 | Siemens | CI-8520 | 6MF2852-0AA00 | Checked | 2 | 11 kV switchroom | 5 x RJ45 | Separate ports per network zone | N/A | - | Not a managed switch. One per controller (rev 1).
D21 | Controller | Flash card, 2 GB | Siemens | SICAM flash card | 6MF1213-1GA05-0AA0 | Checked | 2 | 11 kV switchroom | - | - | N/A | - | One per controller (rev 1).
D22 | I/O | Digital input, 2 x 8 inputs | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 17 | Rows 1 to 6 | Terminal | SICAM I/O link | SICAM I/O link | Rows 1-6 | Confirm DI-8112 is the 110 V DC variant. 24 V: DI-8110, 6MF2811-0AA00. 220 V: DI-8113, 6MF2811-3AA00.
D23 | I/O | Secured command output, 12 outputs | Siemens | DO-8221 | To confirm | To confirm with supplier | 4 | Rows 1, 3, 4 | Terminal | SICAM I/O link | SICAM I/O link | Rows 1, 3, 4 | Breaker open and close with 1-out-of-n check.
D24 | I/O | Digital output, 8 relays, 24-220 V DC / 230 V AC | Siemens | DO-8212 | 6MF2821-2AA00 | Checked | 1 | Row 1 | Terminal | SICAM I/O link | SICAM I/O link | Row 1 | Alarm beacon and controller healthy output, driven by the active controller; the healthy output drops only if both controllers fail (rev 1).
D25 | I/O | Analogue input, 4 x +/-20 mA or +/-10 V | Siemens | AI-8320 | 6MF2832-0AA00 | Checked | 2 | Rows 2, 6 | Terminal | SICAM I/O link | SICAM I/O link | Rows 2, 6 | Row 2: DC bus voltages. Row 6: generator fuel levels.
D26 | I/O | I/O remote interface, electrical, 110-220 V DC | Siemens | CI-8532 | 6MF2853-2AA00 | Checked | 2 | Rows 1, 2 | Copper | SICAM I/O link | SICAM I/O link | Rows 1, 2 | Row 1 moved off the controller backplane onto its own CI-8532 so both controllers reach it (rev 1). 24 V variant: CI-8530, 6MF2853-0AA00.
D27 | I/O | I/O remote interface, optical, 110-220 V DC | Siemens | CI-8533 | To confirm | To confirm with supplier | 4 | Rows 3 to 6 | Fibre | SICAM I/O link, optical | SICAM I/O link | Rows 3-6 | One per remote row: President, Prime Minister, BESS yard, generator area. Confirm fibre type and maximum length. Within about 100 m of the switchroom, CI-8532 on copper may be used instead. 24 V variant: CI-8531.
D28 | I/O | Protocol licences: IEC 104, Modbus TCP client, IEC 61850 client | Siemens | For CP-8050 | By quotation | To confirm with supplier | 2 | - | - | - | N/A | - | One set per controller, including the redundancy function if licensed separately (rev 1).
C. Network, time and security
D29 | Network | Core switch, managed, gigabit, SFP | Moxa | EDS-G512E | EDS-G512E-4GSFP | From memory - confirm | 2 | 11 kV switchroom | RJ45 + SFP | Ethernet, VLANs, ring | N/A | - | Core switch A and B.
D30 | Network | Field and station switch, managed, SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | 5 | MV station, BESS, generators, 2 office stations | RJ45 + SFP | Ethernet, ring | N/A | - | Replaces the unmanaged switch on the existing sheet.
D31 | Network | Fibre transceiver, single-mode, gigabit | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 14 | All switches | LC fibre | - | N/A | - | 7-switch ring, 2 per link.
D32 | Network | Serial to Ethernet gateway | Moxa | MGate MB3170 | MB3170 | From memory - confirm | 2 | Office stations | RS485 + RJ45 | Modbus RTU to Modbus TCP | Modbus TCP | - | Add one more if the generator controllers are RS485 only.
D33 | Network | Firewall with VPN | Fortinet | FortiGate Rugged 60F | FGR-60F | From memory - confirm | 1 | 11 kV switchroom | RJ45 | VPN, off by default | N/A | - | Second unit optional.
D34 | Network | GPS time server with antenna | Meinberg | LANTIME M300 | M300/GPS | From memory - confirm | 1 | 11 kV switchroom | RJ45 | NTP | NTP | -
D35 | Network | Armoured single-mode fibre, 12 core, with patch panels | To suit | - | Length per route | TBC | 3 | Switchroom-President, switchroom-PM, President-PM | LC | - | N/A | - | Third route closes the ring. Rows 5 and 6 use spare cores in the fibre cables to field switches 2 and 3.
D. SCADA computers, power and enclosures
D36 | SCADA | SCADA server, rack industrial PC | Siemens | SIMATIC IPC647E | Configured to order | To confirm with supplier | 2 | Control room | 2 x RJ45 | IEC 60870-5-104 | IEC 60870-5-104 | - | Server A active, server B hot standby.
D37 | SCADA | Operator workstation with two 24-inch monitors | Dell | OptiPlex 7000 series | Configured to order | To confirm with supplier | 1 | Control room | RJ45 | - | N/A | -
D38 | SCADA | Engineering laptop | Dell | Latitude 5430 Rugged | Configured to order | To confirm with supplier | 1 | Control room | RJ45 | - | N/A | -
D39 | SCADA | Power meter | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | From memory - confirm | 3 | LVDB President, LVDB PM, auxiliary board | RJ45 | Modbus TCP | Modbus TCP | -
D40 | SCADA | 24 V DC power supply, 20 A, 1-phase | Siemens | SITOP PSU8200 24 V/20 A | 6EP1336-3BA10 | Checked | 6 | Switchroom, office stations, BESS yard, generator area | - | - | N/A | - | Switches and gateways. Input 85-275 V AC or 88-350 V DC, so it can run from the 110 V DC station battery. Add SITOP UPS1600 if 24 V must ride through loss of input.
D41 | SCADA | UPS for the SCADA cabinet, 3000 VA | APC | Smart-UPS SRT 3000 | SRT3000RMXLI | From memory - confirm | 1 | Control room | RJ45 | SNMP | N/A | - | About 2 hours runtime with battery pack; size at design.
D42 | SCADA | SCADA cabinet, 800 x 2000 x 800 mm | Rittal | VX25 | 8808.000 | From memory - confirm | 1 | 11 kV switchroom | - | - | N/A | Row 2 | Door contact wired to row 2.
D43 | SCADA | Outdoor I/O panel, IP55 minimum | Rittal | AX | Size to suit | TBC | 4 | Office stations, BESS yard, generator area | - | - | N/A | Rows 3-6 | Shaded or air-conditioned where exposed to direct sun.
D44 | SCADA | Alarm sounder and beacon | Pfannenberg | PATROL | Model to suit | TBC | 1 | Control room | Terminal | Hardwired | Hardwired | Row 1
E. Software
D45 | Software | Substation SCADA, redundant | Siemens | SICAM SCC | By quotation | To confirm with supplier | 1 | SCADA servers | - | IEC 60870-5-104 | N/A | - | Licence sized for about 700 signals; includes Operator and Admin roles.
D46 | Software | Controller engineering tool | Siemens | SICAM Device Manager | By quotation | To confirm with supplier | 1 | Engineering laptop | - | - | N/A | -
D47 | Software | Network management | Moxa | MXview One | By quotation | To confirm with supplier | 1 | SCADA server | - | SNMP | N/A | -
D48 | Software | VPN client | Fortinet | FortiClient | - | - | 1 | Remote users | - | - | N/A | -

## Protocol Summary
Primary protocol | Where used | Device lines | Device quantity
IEC 60870-5-104 | CP-8050 to SCADA servers A and B
IEC 61850 | 11 kV protection relays (Modbus TCP if not supported)
Modbus TCP | PLC box, EMS, battery via EMS, generator controllers, power meters, weather logger, UPS, gateways
Modbus RTU | RMU relays ST260E, through MGate gateways
SICAM I/O link | CP-8050 to I/O modules and remote rows (Siemens proprietary)
Hardwired | Status contacts, alarms and commands wired to I/O modules
Power line communication | PV inverters to the PLC box over the AC cables
NTP | Time synchronisation from the GPS time server
Through logger | Weather sensors to the blue'Log
Supervision protocols: SNMP v3 and syslog from switches, firewall and time server to the SCADA servers.

## IO List
Tag | Description | Equipment | Location | Type | I/O row | Module | Module type | Channel | Normal state / range | Alarm level | Operated by | Notes
AH1-CB-OPEN | Circuit breaker open | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 1 | Status | Status | -
AH1-CB-CLSD | Circuit breaker closed | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 2 | Status | Status | -
AH1-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 3 | Normally open | 1 | -
AH1-ES-CLSD | Earth switch closed | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 4 | Status | Status | - | Interlock: blocks remote close
AH1-LR-REM | Local/remote switch in remote | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 5 | Status | Status | - | Interlock: remote commands only in remote
AH1-SPR-CHG | Closing spring charged | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 6 | Normally closed | 3 | -
AH1-GAS-LOW | Gas pressure low | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 7 | Normally open | 2 | -
AH1-RLY-OK | Protection relay healthy | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 8 | Normally closed | 2 | -
AH1-AUX-OK | Control supply healthy | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 9 | Normally closed | 2 | -
AH2-CB-OPEN | Circuit breaker open | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 10 | Status | Status | -
AH2-CB-CLSD | Circuit breaker closed | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 11 | Status | Status | -
AH2-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 12 | Normally open | 1 | -
AH2-ES-CLSD | Earth switch closed | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 13 | Status | Status | - | Interlock: blocks remote close
AH2-LR-REM | Local/remote switch in remote | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 14 | Status | Status | - | Interlock: remote commands only in remote
AH2-SPR-CHG | Closing spring charged | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 15 | Normally closed | 3 | -
AH2-GAS-LOW | Gas pressure low | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 16 | Normally open | 2 | -
AH2-RLY-OK | Protection relay healthy | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 1 | Normally closed | 2 | -
AH2-AUX-OK | Control supply healthy | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 2 | Normally closed | 2 | -
AH3-CB-OPEN | Circuit breaker open | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 3 | Status | Status | -
AH3-CB-CLSD | Circuit breaker closed | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 4 | Status | Status | -
AH3-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 5 | Normally open | 1 | -
AH3-ES-CLSD | Earth switch closed | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 6 | Status | Status | - | Interlock: blocks remote close
AH3-LR-REM | Local/remote switch in remote | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 7 | Status | Status | - | Interlock: remote commands only in remote
AH3-SPR-CHG | Closing spring charged | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 8 | Normally closed | 3 | -
AH3-GAS-LOW | Gas pressure low | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 9 | Normally open | 2 | -
AH3-RLY-OK | Protection relay healthy | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 10 | Normally closed | 2 | -
AH3-AUX-OK | Control supply healthy | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 11 | Normally closed | 2 | -
AH4-CB-OPEN | Circuit breaker open | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 12 | Status | Status | -
AH4-CB-CLSD | Circuit breaker closed | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 13 | Status | Status | -
AH4-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 14 | Normally open | 1 | -
AH4-ES-CLSD | Earth switch closed | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 15 | Status | Status | - | Interlock: blocks remote close
AH4-LR-REM | Local/remote switch in remote | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 16 | Status | Status | - | Interlock: remote commands only in remote
AH4-SPR-CHG | Closing spring charged | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 1 | Normally closed | 3 | -
AH4-GAS-LOW | Gas pressure low | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 2 | Normally open | 2 | -
AH4-RLY-OK | Protection relay healthy | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 3 | Normally closed | 2 | -
AH4-AUX-OK | Control supply healthy | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 4 | Normally closed | 2 | -
AH5-CB-OPEN | Circuit breaker open | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 5 | Status | Status | -
AH5-CB-CLSD | Circuit breaker closed | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 6 | Status | Status | -
AH5-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 7 | Normally open | 1 | -
AH5-ES-CLSD | Earth switch closed | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 8 | Status | Status | - | Interlock: blocks remote close
AH5-LR-REM | Local/remote switch in remote | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 9 | Status | Status | - | Interlock: remote commands only in remote
AH5-SPR-CHG | Closing spring charged | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 10 | Normally closed | 3 | -
AH5-GAS-LOW | Gas pressure low | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 11 | Normally open | 2 | -
AH5-RLY-OK | Protection relay healthy | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 12 | Normally closed | 2 | -
AH5-AUX-OK | Control supply healthy | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 13 | Normally closed | 2 | -
AH6-CB-OPEN | Circuit breaker open | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 14 | Status | Status | -
AH6-CB-CLSD | Circuit breaker closed | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 15 | Status | Status | -
AH6-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 16 | Normally open | 1 | -
AH6-ES-CLSD | Earth switch closed | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 1 | Status | Status | - | Interlock: blocks remote close
AH6-LR-REM | Local/remote switch in remote | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 2 | Status | Status | - | Interlock: remote commands only in remote
AH6-SPR-CHG | Closing spring charged | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 3 | Normally closed | 3 | -
AH6-GAS-LOW | Gas pressure low | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 4 | Normally open | 2 | -
AH6-RLY-OK | Protection relay healthy | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 5 | Normally closed | 2 | -
AH6-AUX-OK | Control supply healthy | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 6 | Normally closed | 2 | -
AH7-CB-OPEN | Circuit breaker open | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 7 | Status | Status | -
AH7-CB-CLSD | Circuit breaker closed | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 8 | Status | Status | -
AH7-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 9 | Normally open | 1 | -
AH7-ES-CLSD | Earth switch closed | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 10 | Status | Status | - | Interlock: blocks remote close
AH7-LR-REM | Local/remote switch in remote | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 11 | Status | Status | - | Interlock: remote commands only in remote
AH7-SPR-CHG | Closing spring charged | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 12 | Normally closed | 3 | -
AH7-GAS-LOW | Gas pressure low | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 13 | Normally open | 2 | -
AH7-RLY-OK | Protection relay healthy | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 14 | Normally closed | 2 | -
AH7-AUX-OK | Control supply healthy | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 15 | Normally closed | 2 | -
AH1-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 1 | Pulse | - | Operator | Select then confirm
AH1-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH2-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH2, PV incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 3 | Pulse | - | Operator | Select then confirm
AH2-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH2, PV incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH3-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 5 | Pulse | - | Operator | Select then confirm
AH3-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH4-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH4, President feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 7 | Pulse | - | Operator | Select then confirm
AH4-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH4, President feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 8 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH5-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 9 | Pulse | - | Operator | Select then confirm
AH5-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 10 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH6-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 11 | Pulse | - | Operator | Select then confirm
AH6-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 12 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH7-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DO | 1 | R1-CO02 | DO-8221 | 1 | Pulse | - | Operator | Select then confirm
AH7-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DO | 1 | R1-CO02 | DO-8221 | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH8-NER-EF | Earth fault current alarm | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 16 | Normally open | 1 | -
AH8-NER-TEMP | Resistor temperature high | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 1 | Normally open | 2 | -
AH8-AUX-OK | Panel supply healthy | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 2 | Normally closed | 2 | -
AH8-CB-OPEN | Circuit breaker open | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 3 | Status | Status | - | Added rev 1. The 11 kV system is earthed only through AH8
AH8-CB-CLSD | Circuit breaker closed | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 4 | Status | Status | - | Added rev 1. Level 1 alarm if open while the busbar is live
AH8-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 5 | Normally open | 1 | - | Added rev 1
AH8-ES-CLSD | Earth switch closed | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 6 | Status | Status | - | Added rev 1
AH8-GAS-LOW | Gas pressure low | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 7 | Normally open | 2 | - | Added rev 1
SYS-BEACON | Critical alarm beacon and sounder | Control room alarm beacon | Control room | DO | 1 | R1-DO01 | DO-8212 | 1 | De-energised | - | Automatic
SYS-CP-HEALTHY | Controller healthy output (watchdog) | SICAM CP-8050 | 11 kV switchroom | DO | 1 | R1-DO01 | DO-8212 | 2 | Energised | - | Automatic
T-AUX-OT-ALM | Oil temperature alarm | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 1 | Normally open | 3 | -
T-AUX-OT-TRIP | Oil temperature trip | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 2 | Normally open | 1 | -
T-AUX-WT-ALM | Winding temperature alarm | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 3 | Normally open | 3 | -
T-AUX-WT-TRIP | Winding temperature trip | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 4 | Normally open | 1 | -
T-AUX-PRD | Pressure relief device operated | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 5 | Normally open | 1 | -
T-AUX-OL-LOW | Oil level low | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 6 | Normally open | 2 | -
T-AUX-FUSE | HV fuse blown (XRNT-3A striker) | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 7 | Normally open | 1 | - | Added rev 1. The fuse is the only HV protection of this transformer
T-INV-OT-ALM | Oil temperature alarm | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 1 | Normally open | 3 | -
T-INV-OT-TRIP | Oil temperature trip | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 2 | Normally open | 1 | -
T-INV-WT-ALM | Winding temperature alarm | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 3 | Normally open | 3 | -
T-INV-WT-TRIP | Winding temperature trip | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 4 | Normally open | 1 | -
T-INV-PRD | Pressure relief device operated | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 5 | Normally open | 1 | -
T-INV-OL-LOW | Oil level low | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 6 | Normally open | 2 | -
PV-ACB-CLSD | PV main LV breaker (ACB 1250 A) closed | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 3 | Status | Status | - | Added rev 1
PV-ACB-TRIP | PV main LV breaker (ACB 1250 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 4 | Normally open | 1 | - | Added rev 1
NB01-MCCB-TRIP | Inverter NB01 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 5 | Normally open | 2 | - | Added rev 1
NB02-MCCB-TRIP | Inverter NB02 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 6 | Normally open | 2 | - | Added rev 1
NB03-MCCB-TRIP | Inverter NB03 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 7 | Normally open | 2 | - | Added rev 1
NB04-MCCB-TRIP | Inverter NB04 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 8 | Normally open | 2 | - | Added rev 1
BESS-ACB-CLSD | Battery main LV breaker (ACB 1000 A) closed | BESS LV breaker 0.69 kV | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 9 | Status | Status | - | Added rev 1
BESS-ACB-TRIP | Battery main LV breaker (ACB 1000 A) tripped | BESS LV breaker 0.69 kV | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 10 | Normally open | 1 | - | Added rev 1
T-DG-OT-ALM | Oil temperature alarm | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 1 | Normally open | 3 | -
T-DG-OT-TRIP | Oil temperature trip | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 2 | Normally open | 1 | -
T-DG-WT-ALM | Winding temperature alarm | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 3 | Normally open | 3 | -
T-DG-WT-TRIP | Winding temperature trip | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 4 | Normally open | 1 | -
T-DG-PRD | Pressure relief device operated | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 5 | Normally open | 1 | -
T-DG-OL-LOW | Oil level low | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 6 | Normally open | 2 | -
GEN-ACB-CLSD | DG step-up transformer LV breaker closed | Generator step-up transformer | Generator area | DI | 6 | R6-DI02 | DI-8112 | 1 | Status | Status | - | Added rev 1
GEN-ACB-TRIP | DG step-up transformer LV breaker tripped | Generator step-up transformer | Generator area | DI | 6 | R6-DI02 | DI-8112 | 2 | Normally open | 1 | - | Added rev 1
DG1-GCB-CLSD | Generator breaker closed | Diesel generator DG1 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 7 | Status | Status | - | Backup to Modbus status
DG1-COM-ALM | Common alarm | Diesel generator DG1 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 8 | Normally open | 2 | -
DG1-ESTOP | Emergency stop active | Diesel generator DG1 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 9 | Normally open | 1 | -
DG1-RUN | Engine running | Diesel generator DG1 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 10 | Status | Status | -
DG2-GCB-CLSD | Generator breaker closed | Diesel generator DG2 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 11 | Status | Status | - | Backup to Modbus status
DG2-COM-ALM | Common alarm | Diesel generator DG2 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 12 | Normally open | 2 | -
DG2-ESTOP | Emergency stop active | Diesel generator DG2 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 13 | Normally open | 1 | -
DG2-RUN | Engine running | Diesel generator DG2 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 14 | Status | Status | -
FIRE-PREALM | Pre-alarm | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 7 | Normally open | 2 | - | Reset at panel only
FIRE-ALM | Fire alarm | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 8 | Normally open | 1 | - | Reset at panel only
FIRE-FLT | System fault | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 9 | Normally open | 2 | - | Reset at panel only
FIRE-REL | Suppression released | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 10 | Normally open | 1 | - | Reset at panel only
FIRE-AGENT-LOW | Agent pressure low | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 11 | Normally open | 2 | - | Reset at panel only
FIRE-ISOL | System isolated | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 12 | Normally open | 2 | - | Reset at panel only
FIRE-MAN-REL | Manual release activated | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 13 | Normally open | 1 | - | Reset at panel only
FIRE-PSU-FLT | Panel supply fault | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 14 | Normally open | 2 | - | Reset at panel only
AUXLV-INC-CLSD | Auxiliary LV incomer closed | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 7 | Status | Status | -
AUXLV-INC-TRIP | Auxiliary LV incomer tripped | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 8 | Normally open | 2 | -
AUXLV-SPD-FLT | Surge arrester failed | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 9 | Normally open | 3 | -
UPS-ON-BATT | UPS on battery | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 10 | Normally open | 2 | -
UPS-BATT-LOW | UPS battery low | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 11 | Normally open | 1 | -
UPS-FLT | UPS fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 12 | Normally open | 2 | -
UPS-BYPASS | UPS on bypass | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 13 | Normally open | 3 | -
DC-CHG-FLT | DC charger fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 14 | Normally open | 2 | -
DC-EARTH-FLT | DC earth fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 15 | Normally open | 2 | -
DC-UV | DC bus undervoltage | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 16 | Normally open | 1 | -
SWR-HVAC-FLT | Switchroom air conditioning fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 1 | Normally open | 3 | -
SWR-TEMP-HI | Switchroom temperature high | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 2 | Normally open | 3 | -
ESTOP-SWR | Plant emergency stop pressed, switchroom | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 3 | Normally open | 1 | -
DOOR-SCADA | SCADA cabinet door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 4 | Normally open | 3 | -
DOOR-SWR | Switchroom door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 5 | Normally open | 3 | -
DOOR-GIS | 11 kV switchgear room door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 6 | Normally open | 3 | -
ESTOP-BESS | Plant emergency stop pressed, BESS area | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 15 | Normally open | 1 | -
DOOR-BESS | BESS container door open | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 16 | Normally open | 3 | -
YARD-PNL-SUP-OK | Yard I/O panel supply healthy | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 1 | Normally closed | 2 | -
YARD-PNL-DOOR | Yard I/O panel door open | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 2 | Normally open | 3 | -
GEN-PNL-SUP-OK | Generator I/O panel supply healthy | Emergency stops, doors and I/O panels | Generator area | DI | 6 | R6-DI01 | DI-8112 | 15 | Normally closed | 2 | -
GEN-PNL-DOOR | Generator I/O panel door open | Emergency stops, doors and I/O panels | Generator area | DI | 6 | R6-DI01 | DI-8112 | 16 | Normally open | 3 | -
DG1-FUEL | Fuel tank level | Diesel generator DG1 | Generator area | AI | 6 | R6-AI01 | AI-8320 | 1 | 4-20 mA = 0-100 % | 3 below 20 % | -
DG2-FUEL | Fuel tank level | Diesel generator DG2 | Generator area | AI | 6 | R6-AI01 | AI-8320 | 2 | 4-20 mA = 0-100 % | 3 below 20 % | -
DC-110-V | 110 V DC bus voltage | Auxiliary supplies and UPS | 11 kV switchroom | AI | 2 | R2-AI01 | AI-8320 | 1 | 4-20 mA = 0-150 V | 2 outside limits | -
DC-24-V | 24 V DC bus voltage | Auxiliary supplies and UPS | 11 kV switchroom | AI | 2 | R2-AI01 | AI-8320 | 2 | 4-20 mA = 0-36 V | 2 outside limits | -
PRS-RS1-OPEN | Ring switch 1 open | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 1 | Status | Status | -
PRS-RS1-CLSD | Ring switch 1 closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 2 | Status | Status | -
PRS-RS1-ES | Ring switch 1 earth switch closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 3 | Status | Status | -
PRS-RS2-OPEN | Ring switch 2 open | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 4 | Status | Status | -
PRS-RS2-CLSD | Ring switch 2 closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 5 | Status | Status | -
PRS-RS2-ES | Ring switch 2 earth switch closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 6 | Status | Status | -
PRS-CB-OPEN | Transformer breaker open | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 7 | Status | Status | -
PRS-CB-CLSD | Transformer breaker closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 8 | Status | Status | -
PRS-CB-ES | Transformer breaker earth switch closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 9 | Status | Status | -
PRS-CB-TRIP | Transformer breaker tripped by ST260E | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 10 | Normally open | 1 | -
PRS-GAS-LOW | RMU gas pressure low | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 11 | Normally open | 2 | -
PRS-LR-REM | RMU local/remote in remote | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 12 | Status | Status | -
PRS-FPI | Fault passage indicator operated | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 13 | Normally open | 2 | -
PRS-TX-OT-ALM | Oil temperature alarm | President station transformer 630 kVA | President station | DI | 3 | R3-DI01 | DI-8112 | 14 | Normally open | 3 | -
PRS-TX-OT-TRIP | Oil temperature trip | President station transformer 630 kVA | President station | DI | 3 | R3-DI01 | DI-8112 | 15 | Normally open | 1 | -
PRS-TX-WT-ALM | Winding temperature alarm | President station transformer 630 kVA | President station | DI | 3 | R3-DI01 | DI-8112 | 16 | Normally open | 3 | -
PRS-TX-WT-TRIP | Winding temperature trip | President station transformer 630 kVA | President station | DI | 3 | R3-DI02 | DI-8112 | 1 | Normally open | 1 | -
PRS-TX-PRD | Pressure relief device operated | President station transformer 630 kVA | President station | DI | 3 | R3-DI02 | DI-8112 | 2 | Normally open | 1 | -
PRS-TX-OL-LOW | Oil level low | President station transformer 630 kVA | President station | DI | 3 | R3-DI02 | DI-8112 | 3 | Normally open | 2 | -
PRS-LV-INC-CLSD | LV incomer closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 4 | Status | Status | -
PRS-LV-INC-TRIP | LV incomer tripped | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 5 | Normally open | 2 | -
PRS-LV-F01-CLSD | Outgoing way 1 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 6 | Status | Status | -
PRS-LV-F02-CLSD | Outgoing way 2 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 7 | Status | Status | -
PRS-LV-F03-CLSD | Outgoing way 3 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 8 | Status | Status | -
PRS-LV-F04-CLSD | Outgoing way 4 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 9 | Status | Status | -
PRS-LV-F05-CLSD | Outgoing way 5 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 10 | Status | Status | -
PRS-LV-F06-CLSD | Outgoing way 6 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 11 | Status | Status | -
PRS-LV-F07-CLSD | Outgoing way 7 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 12 | Status | Status | -
PRS-LV-F08-CLSD | Outgoing way 8 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 13 | Status | Status | -
PRS-LV-F09-CLSD | Outgoing way 9 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 14 | Status | Status | -
PRS-LV-F10-CLSD | Outgoing way 10 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 15 | Status | Status | -
PRS-LV-SPD-FLT | Surge arrester failed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 16 | Normally open | 3 | -
PRS-PNL-SUP-OK | I/O panel supply healthy | President station LVDB | President station | DI | 3 | R3-DI03 | DI-8112 | 1 | Normally closed | 2 | -
PRS-UPS-ON-BATT | RMU UPS 2 kVA on battery | President station RMU | President station | DI | 3 | R3-DI03 | DI-8112 | 2 | Normally open | 2 | - | Added rev 1. UPS shown on the transformer stations drawing
PRS-UPS-FLT | RMU UPS 2 kVA fault | President station RMU | President station | DI | 3 | R3-DI03 | DI-8112 | 3 | Normally open | 2 | - | Added rev 1
PRS-RS1-OPEN-CMD | Open ring switch 1 | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 1 | Pulse | - | Operator | Select then confirm
PRS-RS1-CLOSE-CMD | Close ring switch 1 | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed
PRS-RS2-OPEN-CMD | Open ring switch 2 | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 3 | Pulse | - | Operator | Select then confirm
PRS-RS2-CLOSE-CMD | Close ring switch 2 | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed
PRS-CB-OPEN-CMD | Open transformer breaker | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 5 | Pulse | - | Operator | Select then confirm
PRS-CB-CLOSE-CMD | Close transformer breaker | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed
PRS-LV-INC-OPEN-CMD | Open LV incomer | President station LVDB | President station | DO | 3 | R3-CO01 | DO-8221 | 7 | Pulse | - | Operator | Select then confirm
PRS-LV-INC-CLOSE-CMD | Close LV incomer | President station LVDB | President station | DO | 3 | R3-CO01 | DO-8221 | 8 | Pulse | - | Operator | Select then confirm
PMS-RS1-OPEN | Ring switch 1 open | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 1 | Status | Status | -
PMS-RS1-CLSD | Ring switch 1 closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 2 | Status | Status | -
PMS-RS1-ES | Ring switch 1 earth switch closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 3 | Status | Status | -
PMS-RS2-OPEN | Ring switch 2 open | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 4 | Status | Status | -
PMS-RS2-CLSD | Ring switch 2 closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 5 | Status | Status | -
PMS-RS2-ES | Ring switch 2 earth switch closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 6 | Status | Status | -
PMS-CB-OPEN | Transformer breaker open | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 7 | Status | Status | -
PMS-CB-CLSD | Transformer breaker closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 8 | Status | Status | -
PMS-CB-ES | Transformer breaker earth switch closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 9 | Status | Status | -
PMS-CB-TRIP | Transformer breaker tripped by ST260E | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 10 | Normally open | 1 | -
PMS-GAS-LOW | RMU gas pressure low | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 11 | Normally open | 2 | -
PMS-LR-REM | RMU local/remote in remote | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 12 | Status | Status | -
PMS-FPI | Fault passage indicator operated | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 13 | Normally open | 2 | -
PMS-TX-OT-ALM | Oil temperature alarm | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 14 | Normally open | 3 | -
PMS-TX-OT-TRIP | Oil temperature trip | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 15 | Normally open | 1 | -
PMS-TX-WT-ALM | Winding temperature alarm | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 16 | Normally open | 3 | -
PMS-TX-WT-TRIP | Winding temperature trip | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 1 | Normally open | 1 | -
PMS-TX-PRD | Pressure relief device operated | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 2 | Normally open | 1 | -
PMS-TX-OL-LOW | Oil level low | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 3 | Normally open | 2 | -
PMS-LV-INC-CLSD | LV incomer closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 4 | Status | Status | -
PMS-LV-INC-TRIP | LV incomer tripped | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 5 | Normally open | 2 | -
PMS-LV-F01-CLSD | Outgoing way 1 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 6 | Status | Status | -
PMS-LV-F02-CLSD | Outgoing way 2 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 7 | Status | Status | -
PMS-LV-F03-CLSD | Outgoing way 3 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 8 | Status | Status | -
PMS-LV-F04-CLSD | Outgoing way 4 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 9 | Status | Status | -
PMS-LV-F05-CLSD | Outgoing way 5 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 10 | Status | Status | -
PMS-LV-F06-CLSD | Outgoing way 6 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 11 | Status | Status | -
PMS-LV-F07-CLSD | Outgoing way 7 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 12 | Status | Status | -
PMS-LV-F08-CLSD | Outgoing way 8 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 13 | Status | Status | -
PMS-LV-F09-CLSD | Outgoing way 9 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 14 | Status | Status | -
PMS-LV-F10-CLSD | Outgoing way 10 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 15 | Status | Status | -
PMS-LV-SPD-FLT | Surge arrester failed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 16 | Normally open | 3 | -
PMS-PNL-SUP-OK | I/O panel supply healthy | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI03 | DI-8112 | 1 | Normally closed | 2 | -
PMS-UPS-ON-BATT | RMU UPS 2 kVA on battery | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI03 | DI-8112 | 2 | Normally open | 2 | - | Added rev 1. UPS shown on the transformer stations drawing
PMS-UPS-FLT | RMU UPS 2 kVA fault | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI03 | DI-8112 | 3 | Normally open | 2 | - | Added rev 1
PMS-RS1-OPEN-CMD | Open ring switch 1 | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 1 | Pulse | - | Operator | Select then confirm
PMS-RS1-CLOSE-CMD | Close ring switch 1 | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed
PMS-RS2-OPEN-CMD | Open ring switch 2 | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 3 | Pulse | - | Operator | Select then confirm
PMS-RS2-CLOSE-CMD | Close ring switch 2 | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed
PMS-CB-OPEN-CMD | Open transformer breaker | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 5 | Pulse | - | Operator | Select then confirm
PMS-CB-CLOSE-CMD | Close transformer breaker | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed
PMS-LV-INC-OPEN-CMD | Open LV incomer | Prime Minister station LVDB | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 7 | Pulse | - | Operator | Select then confirm
PMS-LV-INC-CLOSE-CMD | Close LV incomer | Prime Minister station LVDB | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 8 | Pulse | - | Operator | Select then confirm

## IO Summary
I/O row | Location | Module | Module type | Channels | Used | Spare | Spare %
1 | 11 kV switchroom (local) | R1-DI01 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-DI02 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-DI03 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-DI04 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-DI05 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-CO01 | DO-8221 | 12
1 | 11 kV switchroom (local) | R1-CO02 | DO-8221 | 12
1 | 11 kV switchroom (local) | R1-DO01 | DO-8212 | 8
2 | 11 kV switchroom (CI-8532) | R2-DI01 | DI-8112 | 16
2 | 11 kV switchroom (CI-8532) | R2-DI02 | DI-8112 | 16
2 | 11 kV switchroom (CI-8532) | R2-AI01 | AI-8320 | 4
3 | President station (CI-8533) | R3-DI01 | DI-8112 | 16
3 | President station (CI-8533) | R3-DI02 | DI-8112 | 16
3 | President station (CI-8533) | R3-DI03 | DI-8112 | 16
3 | President station (CI-8533) | R3-CO01 | DO-8221 | 12
4 | Prime Minister station (CI-8533) | R4-DI01 | DI-8112 | 16
4 | Prime Minister station (CI-8533) | R4-DI02 | DI-8112 | 16
4 | Prime Minister station (CI-8533) | R4-DI03 | DI-8112 | 16
4 | Prime Minister station (CI-8533) | R4-CO01 | DO-8221 | 12
5 | BESS and inverter transformer yard (CI-8533) | R5-DI01 | DI-8112 | 16
5 | BESS and inverter transformer yard (CI-8533) | R5-DI02 | DI-8112 | 16
6 | Generator area (CI-8533) | R6-DI01 | DI-8112 | 16
6 | Generator area (CI-8533) | R6-DI02 | DI-8112 | 16
6 | Generator area (CI-8533) | R6-AI01 | AI-8320 | 4
Totals by module type
Module type | Description | Modules | Channels | Used | Spare | Spare %
DI-8112 | Digital input, 16
DO-8221 | Secured command output, 12
DO-8212 | Relay output, 8
AI-8320 | Analogue input, 4
Total
Hardwired signals by type
Type | Meaning | Signals
DI | Digital input (status, alarm)
DO | Digital output (command)
AI | Analogue input (4-20 mA)
Total

## IO Rows
I/O row | Location | Remote interface | Product number | Link to CP-8050 | Equipment wired to this row | I/O modules | Hardwired signals | Spare channels
1 | 11 kV switchroom, SCADA cabinet | CI-8532 (electrical) | 6MF2853-2AA00 | Copper, inside the cabinet | 11 kV panels AH1 to AH8, alarm beacon, controller watchdog
2 | 11 kV switchroom, SCADA cabinet | CI-8532 (electrical) | 6MF2853-2AA00 | Copper, inside the cabinet | Auxiliary transformer, auxiliary LV board, UPS, DC supplies, switchroom E-stop and doors
3 | President office transformer station | CI-8533 (optical) | To confirm | Fibre pair, laid with the 11 kV cable | RMU, 630 kVA transformer, LVDB
4 | Prime Minister office transformer station | CI-8533 (optical) | To confirm | Fibre pair, laid with the 11 kV cable | RMU, 630 kVA transformer, LVDB
5 | BESS and inverter transformer yard | CI-8533 (optical) | To confirm | Spare fibre pair in the field switch 2 cable | Inverter transformer, battery fire panel, BESS E-stop and door, panel supervision
6 | Generator area | CI-8533 (optical) | To confirm | Spare fibre pair in the field switch 3 cable | DG1 and DG2 status and fuel level, DG step-up transformer, panel supervision
Total
Each row has its own interface module and is reached by both controllers of the hot standby pair; only the active controller reads inputs and drives outputs. Each remote row is a small panel near its equipment, with field contacts wired a short distance to that panel.
Rows within about 100 m of the switchroom may use CI-8532 on copper instead of CI-8533 on fibre. Fibre is preferred between buildings for surge and earth-potential immunity.
Confirm with Siemens: fibre type and maximum length for CI-8533, and whether the remote link can share a fibre cable with the plant network on separate cores. Also confirm how the I/O rows connect to both controllers of the redundant pair.
The CP-8050 accepts up to 16 I/O rows of 8 modules, so the design uses 6 of 16 rows.

## Comms Points
Device | Source / protocol | Point | Direction | Data type | Unit | Devices | Points each | Total points | Operated by | Notes
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Active power | Read | Measured | kW | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Reactive power | Read | Measured | kvar | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | 4 | 3 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | AC current L1, L2, L3 (3 points) | Read | Measured | A | 4 | 3 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Frequency | Read | Measured | Hz | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Power factor | Read | Measured | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC voltage | Read | Measured | V | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC current | Read | Measured | A | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC power | Read | Measured | kW | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Energy today | Read | Counter | kWh | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Energy total | Read | Counter | MWh | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Internal temperature | Read | Measured | deg C | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Insulation resistance | Read | Measured | kohm | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Operating state | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Fault code | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Alarm code | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Communication healthy | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Active power limit | Write | Setpoint | % | 4 | 1 |  | Admin | Normally set by the EMS; write only if the EMS allows
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Start / stop | Write | Command | - | 4 | 1 |  | Admin
Embedded EMS | Modbus TCP | Plant active power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Plant reactive power | Read | Measured | kvar | 1 | 1 |  | -
Embedded EMS | Modbus TCP | PV total power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | BESS power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Generator total power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Load power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Bus voltage | Read | Measured | kV | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Bus frequency | Read | Measured | Hz | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Operating mode | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS state | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS summary alarm | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Generator start request | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | PV curtailment active | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS heartbeat | Read/Write | Counter | - | 1 | 1 |  | Automatic | Link supervision
Embedded EMS | Modbus TCP | Operating mode select | Write | Command | - | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | State of charge minimum | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | State of charge maximum | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | Generator start threshold | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | Generator stop threshold | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | BESS power limit | Write | Setpoint | kW | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | BESS C-rate limit enable / disable | Write | Command | - | 1 | 1 |  | Admin | Calibration only; available only if the EMS exposes it
Embedded EMS | Modbus TCP | Fault reset, level 3 | Write | Command | - | 1 | 1 |  | Operator
Embedded EMS | Modbus TCP | Fault reset, levels 1 and 2 | Write | Command | - | 1 | 1 |  | Admin
Battery system ST3340UX | Through the EMS, Modbus TCP | State of charge | Read | Measured | % | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | State of health | Read | Measured | % | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC voltage | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC current | Read | Measured | A | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Active power | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Reactive power | Read | Measured | kvar | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell voltage maximum | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell voltage minimum | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell temperature maximum | Read | Measured | deg C | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell temperature minimum | Read | Measured | deg C | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Charge power limit | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Discharge power limit | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Energy charged total | Read | Counter | MWh | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Energy discharged total | Read | Counter | MWh | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Converter state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery management state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Racks online | Read | Measured | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC contactors closed | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cooling system state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 1 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 2 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 3 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Container fire status | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery combiner panel DC switch closed (2 points) | Read | Status | - | 1 | 2 |  | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery combiner panel fuse blown (2 points) | Read | Status | - | 1 | 2 |  | - | Added rev 1. As above
Generator controller DG1, DG2 | Modbus TCP or RTU | Voltage L1, L2, L3 (3 points) | Read | Measured | V | 2 | 3 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Current L1, L2, L3 (3 points) | Read | Measured | A | 2 | 3 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Active power | Read | Measured | kW | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Reactive power | Read | Measured | kvar | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Power factor | Read | Measured | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Frequency | Read | Measured | Hz | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Oil pressure | Read | Measured | kPa | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Coolant temperature | Read | Measured | deg C | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Starter battery voltage | Read | Measured | V | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Fuel level | Read | Measured | % | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Running hours | Read | Counter | h | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Number of starts | Read | Counter | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Energy total | Read | Counter | MWh | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Controller mode | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Breaker status | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Warning | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Shutdown alarm | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Start | Write | Command | - | 2 | 1 |  | Operator | Only in manual mode
Generator controller DG1, DG2 | Modbus TCP or RTU | Stop | Write | Command | - | 2 | 1 |  | Operator | Only in manual mode
Generator controller DG1, DG2 | Modbus TCP or RTU | Mode auto / manual | Write | Command | - | 2 | 1 |  | Admin
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Phase current L1, L2, L3 (3 points) | Read | Measured | A | 7 | 3 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Earth current | Read | Measured | A | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | 7 | 3 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Active power | Read | Measured | kW | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Reactive power | Read | Measured | kvar | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Power factor | Read | Measured | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Frequency | Read | Measured | Hz | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Energy import | Read | Counter | MWh | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Energy export | Read | Counter | MWh | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Breaker position | Read | Double point | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Overcurrent trip (50/51) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Earth fault trip (50N/51N) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Under / overvoltage trip (27/59) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Frequency trip (81) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Relay healthy | Read | Status | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Disturbance record available | Read | Status | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Trip circuit supervision alarm | Read | Status | - | 7 | 1 |  | - | Added rev 1
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Sensitive earth fault trip (51G) | Read | Event | - | 6 | 1 |  | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Reverse power trip (32), AH1 generator incomer | Read | Event | - | 1 | 1 |  | - | Added rev 1. Protects the generators against reverse power from PV and battery
RMU relay ST260E | Modbus RTU through MGate | Phase current L1, L2, L3 (3 points) | Read | Measured | A | 2 | 3 |  | -
RMU relay ST260E | Modbus RTU through MGate | Earth current | Read | Measured | A | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through MGate | Breaker position | Read | Double point | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through MGate | Overcurrent trip | Read | Event | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through MGate | Earth fault trip | Read | Event | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through MGate | Relay healthy | Read | Status | - | 2 | 1 |  | -
Power meter PM5560 | Modbus TCP | Voltage L-N, 3 phases (3 points) | Read | Measured | V | 3 | 3 |  | -
Power meter PM5560 | Modbus TCP | Current, 3 phases (3 points) | Read | Measured | A | 3 | 3 |  | -
Power meter PM5560 | Modbus TCP | Active power | Read | Measured | kW | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Reactive power | Read | Measured | kvar | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Apparent power | Read | Measured | kVA | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Power factor | Read | Measured | - | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Frequency | Read | Measured | Hz | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Active energy | Read | Counter | kWh | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Reactive energy | Read | Counter | kvarh | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Voltage THD | Read | Measured | % | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Current THD | Read | Measured | % | 3 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Plane-of-array irradiance | Read | Measured | W/m2 | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Wind speed | Read | Measured | m/s | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Wind direction | Read | Measured | deg | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Ambient temperature | Read | Measured | deg C | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Module temperature | Read | Measured | deg C | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Logger healthy | Read | Status | - | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Input voltage | Read | Measured | V | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Output load | Read | Measured | % | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Battery charge | Read | Measured | % | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Runtime remaining | Read | Measured | min | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | On battery | Read | Status | - | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Fault | Read | Status | - | 1 | 1 |  | -
Network switches (core and field) | SNMP v3 | Device healthy | Read | Status | - | 7 | 1 |  | -
Network switches (core and field) | SNMP v3 | Ring status | Read | Status | - | 7 | 1 |  | -
Firewall and GPS time server | SNMP v3 | Device healthy | Read | Status | - | 2 | 1 |  | -
Firewall and GPS time server | SNMP v3 | Time synchronised / VPN session active | Read | Status | - | 2 | 1 |  | -
PLC box | Modbus TCP | Communication healthy per inverter (4 points) | Read | Status | - | 1 | 4 |  | -
SICAM CP-8050 internal | Internal | Controller healthy (controllers A and B) | Read | Status | - | 2 | 1 |  | - | Added rev 1. One per controller of the hot standby pair
SICAM CP-8050 internal | Internal | Power supply 1 healthy (controllers A and B) | Read | Status | - | 2 | 1 |  | - | Added rev 1. One per controller of the hot standby pair
SICAM CP-8050 internal | Internal | Power supply 2 healthy (controllers A and B) | Read | Status | - | 2 | 1 |  | - | Added rev 1. One per controller of the hot standby pair
SICAM CP-8050 internal | Internal | I/O row 1 link healthy | Read | Status | - | 1 | 1 |  | - | Added rev 1. Row 1 now has its own CI-8532 interface, so both controllers reach it
SICAM CP-8050 internal | Internal | I/O row 2 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 3 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 4 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 5 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 6 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | Link to each communication device healthy (8 links) | Read | Status | - | 1 | 8 |  | -
SICAM CP-8050 internal | Internal | Controller active (controllers A and B) | Read | Status | - | 2 | 1 |  | - | Added rev 1. Shows which controller is in control
SICAM CP-8050 internal | Internal | Standby controller synchronised and ready | Read | Status | - | 1 | 1 |  | - | Added rev 1. Off means a failure of the active controller would not be covered
SICAM CP-8050 internal | Internal | Controller switchover occurred | Read | Event | - | 1 | 1 |  | - | Added rev 1. Logged with time; resets on acknowledgement
Total
Read
Write
Typical points only. Replace each block with the vendor's point table when received.

## Comms Point List
Tag | Device | Point | Direction | Data type | Unit | Source / protocol | Alarm level | Alarm when | Operated by | Notes
NB01-P | PV inverter NB01 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB01-Q | PV inverter NB01 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB01-U-L1 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-U-L2 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-U-L3 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-I-L1 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-I-L2 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-I-L3 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-F | PV inverter NB01 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB01-PF | PV inverter NB01 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB01-U-DC | PV inverter NB01 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-I-DC | PV inverter NB01 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-P-DC | PV inverter NB01 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB01-E-DAY | PV inverter NB01 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB01-E-TOT | PV inverter NB01 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB01-T-INT | PV inverter NB01 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB01-R-ISO | PV inverter NB01 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB01-STATE | PV inverter NB01 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-FLT-CODE | PV inverter NB01 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-ALM-CODE | PV inverter NB01 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-COMM-OK | PV inverter NB01 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB01-P-LIM-SP | PV inverter NB01 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB01-START-STOP-CMD | PV inverter NB01 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB02-P | PV inverter NB02 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB02-Q | PV inverter NB02 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB02-U-L1 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-U-L2 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-U-L3 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-I-L1 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-I-L2 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-I-L3 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-F | PV inverter NB02 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB02-PF | PV inverter NB02 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB02-U-DC | PV inverter NB02 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-I-DC | PV inverter NB02 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-P-DC | PV inverter NB02 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB02-E-DAY | PV inverter NB02 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB02-E-TOT | PV inverter NB02 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB02-T-INT | PV inverter NB02 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB02-R-ISO | PV inverter NB02 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB02-STATE | PV inverter NB02 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-FLT-CODE | PV inverter NB02 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-ALM-CODE | PV inverter NB02 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-COMM-OK | PV inverter NB02 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB02-P-LIM-SP | PV inverter NB02 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB02-START-STOP-CMD | PV inverter NB02 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB03-P | PV inverter NB03 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB03-Q | PV inverter NB03 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB03-U-L1 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-U-L2 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-U-L3 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-I-L1 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-I-L2 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-I-L3 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-F | PV inverter NB03 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB03-PF | PV inverter NB03 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB03-U-DC | PV inverter NB03 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-I-DC | PV inverter NB03 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-P-DC | PV inverter NB03 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB03-E-DAY | PV inverter NB03 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB03-E-TOT | PV inverter NB03 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB03-T-INT | PV inverter NB03 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB03-R-ISO | PV inverter NB03 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB03-STATE | PV inverter NB03 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-FLT-CODE | PV inverter NB03 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-ALM-CODE | PV inverter NB03 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-COMM-OK | PV inverter NB03 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB03-P-LIM-SP | PV inverter NB03 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB03-START-STOP-CMD | PV inverter NB03 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB04-P | PV inverter NB04 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB04-Q | PV inverter NB04 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB04-U-L1 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-U-L2 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-U-L3 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-I-L1 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-I-L2 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-I-L3 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-F | PV inverter NB04 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB04-PF | PV inverter NB04 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB04-U-DC | PV inverter NB04 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-I-DC | PV inverter NB04 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-P-DC | PV inverter NB04 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB04-E-DAY | PV inverter NB04 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB04-E-TOT | PV inverter NB04 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB04-T-INT | PV inverter NB04 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB04-R-ISO | PV inverter NB04 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB04-STATE | PV inverter NB04 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-FLT-CODE | PV inverter NB04 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-ALM-CODE | PV inverter NB04 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-COMM-OK | PV inverter NB04 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB04-P-LIM-SP | PV inverter NB04 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB04-START-STOP-CMD | PV inverter NB04 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
EMS-P-PLANT | Embedded EMS | Plant active power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-Q-PLANT | Embedded EMS | Plant reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
EMS-P-PV | Embedded EMS | PV total power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-BESS | Embedded EMS | BESS power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-GEN | Embedded EMS | Generator total power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-LOAD | Embedded EMS | Load power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-U-BUS | Embedded EMS | Bus voltage | Read | Measured | kV | Modbus TCP | - | - | -
EMS-F-BUS | Embedded EMS | Bus frequency | Read | Measured | Hz | Modbus TCP | - | - | -
EMS-MODE | Embedded EMS | Operating mode | Read | Status | - | Modbus TCP | Status | - | -
EMS-STATE | Embedded EMS | EMS state | Read | Status | - | Modbus TCP | Status | - | -
EMS-ALM | Embedded EMS | EMS summary alarm | Read | Status | - | Modbus TCP | 2 | On | -
EMS-GEN-START-REQ | Embedded EMS | Generator start request | Read | Status | - | Modbus TCP | 3 | On | -
EMS-PV-CURT | Embedded EMS | PV curtailment active | Read | Status | - | Modbus TCP | 3 | On | -
EMS-HEARTBEAT | Embedded EMS | EMS heartbeat | Read/Write | Counter | - | Modbus TCP | - | - | Automatic | Link supervision
EMS-MODE-CMD | Embedded EMS | Operating mode select | Write | Command | - | Modbus TCP | - | - | Admin
EMS-SOC-MIN-SP | Embedded EMS | State of charge minimum | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-SOC-MAX-SP | Embedded EMS | State of charge maximum | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-GEN-START-SP | Embedded EMS | Generator start threshold | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-GEN-STOP-SP | Embedded EMS | Generator stop threshold | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-P-BESS-LIM-SP | Embedded EMS | BESS power limit | Write | Setpoint | kW | Modbus TCP | - | - | Admin
EMS-CRATE-CMD | Embedded EMS | BESS C-rate limit enable / disable | Write | Command | - | Modbus TCP | - | - | Admin | Calibration only; available only if the EMS exposes it
EMS-RESET-L3-CMD | Embedded EMS | Fault reset, level 3 | Write | Command | - | Modbus TCP | - | - | Operator
EMS-RESET-L12-CMD | Embedded EMS | Fault reset, levels 1 and 2 | Write | Command | - | Modbus TCP | - | - | Admin
BESS-SOC | Battery system ST3340UX | State of charge | Read | Measured | % | Through the EMS, Modbus TCP | - | - | -
BESS-SOH | Battery system ST3340UX | State of health | Read | Measured | % | Through the EMS, Modbus TCP | - | - | -
BESS-U-DC | Battery system ST3340UX | DC voltage | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-I-DC | Battery system ST3340UX | DC current | Read | Measured | A | Through the EMS, Modbus TCP | - | - | -
BESS-P | Battery system ST3340UX | Active power | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-Q | Battery system ST3340UX | Reactive power | Read | Measured | kvar | Through the EMS, Modbus TCP | - | - | -
BESS-U-CELL-MAX | Battery system ST3340UX | Cell voltage maximum | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-U-CELL-MIN | Battery system ST3340UX | Cell voltage minimum | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-T-CELL-MAX | Battery system ST3340UX | Cell temperature maximum | Read | Measured | deg C | Through the EMS, Modbus TCP | - | - | -
BESS-T-CELL-MIN | Battery system ST3340UX | Cell temperature minimum | Read | Measured | deg C | Through the EMS, Modbus TCP | - | - | -
BESS-P-CHG-LIM | Battery system ST3340UX | Charge power limit | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-P-DIS-LIM | Battery system ST3340UX | Discharge power limit | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-E-CHG | Battery system ST3340UX | Energy charged total | Read | Counter | MWh | Through the EMS, Modbus TCP | - | - | -
BESS-E-DIS | Battery system ST3340UX | Energy discharged total | Read | Counter | MWh | Through the EMS, Modbus TCP | - | - | -
BESS-PCS-STATE | Battery system ST3340UX | Converter state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-BMS-STATE | Battery system ST3340UX | Battery management state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-RACKS-ON | Battery system ST3340UX | Racks online | Read | Measured | - | Through the EMS, Modbus TCP | - | - | -
BESS-DC-CONT | Battery system ST3340UX | DC contactors closed | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-COOL-STATE | Battery system ST3340UX | Cooling system state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-ALM-L1 | Battery system ST3340UX | Alarm level 1 | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | -
BESS-ALM-L2 | Battery system ST3340UX | Alarm level 2 | Read | Status | - | Through the EMS, Modbus TCP | 2 | On | -
BESS-ALM-L3 | Battery system ST3340UX | Alarm level 3 | Read | Status | - | Through the EMS, Modbus TCP | 3 | On | -
BESS-FIRE | Battery system ST3340UX | Container fire status | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | -
BESS-BCP1-SW-CLSD | Battery system ST3340UX | Battery combiner panel DC switch closed (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 2 | Off | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
BESS-BCP2-SW-CLSD | Battery system ST3340UX | Battery combiner panel DC switch closed (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 2 | Off | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
BESS-BCP1-FUSE | Battery system ST3340UX | Battery combiner panel fuse blown (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | - | Added rev 1. As above
BESS-BCP2-FUSE | Battery system ST3340UX | Battery combiner panel fuse blown (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | - | Added rev 1. As above
DG1-U-L1 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-U-L2 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-U-L3 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-I-L1 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-I-L2 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-I-L3 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-P | Generator controller DG1 | Active power | Read | Measured | kW | Modbus TCP or RTU | - | - | -
DG1-Q | Generator controller DG1 | Reactive power | Read | Measured | kvar | Modbus TCP or RTU | - | - | -
DG1-PF | Generator controller DG1 | Power factor | Read | Measured | - | Modbus TCP or RTU | - | - | -
DG1-F | Generator controller DG1 | Frequency | Read | Measured | Hz | Modbus TCP or RTU | - | - | -
DG1-OIL-P | Generator controller DG1 | Oil pressure | Read | Measured | kPa | Modbus TCP or RTU | - | - | -
DG1-COOL-T | Generator controller DG1 | Coolant temperature | Read | Measured | deg C | Modbus TCP or RTU | - | - | -
DG1-BATT-U | Generator controller DG1 | Starter battery voltage | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-FUEL-COM | Generator controller DG1 | Fuel level | Read | Measured | % | Modbus TCP or RTU | - | - | - | Communicated copy of hardwired signal DG1-FUEL
DG1-HOURS | Generator controller DG1 | Running hours | Read | Counter | h | Modbus TCP or RTU | - | - | -
DG1-STARTS | Generator controller DG1 | Number of starts | Read | Counter | - | Modbus TCP or RTU | - | - | -
DG1-E-TOT | Generator controller DG1 | Energy total | Read | Counter | MWh | Modbus TCP or RTU | - | - | -
DG1-MODE | Generator controller DG1 | Controller mode | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG1-GCB | Generator controller DG1 | Breaker status | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG1-WARN | Generator controller DG1 | Warning | Read | Status | - | Modbus TCP or RTU | 3 | On | -
DG1-SHUTDOWN | Generator controller DG1 | Shutdown alarm | Read | Status | - | Modbus TCP or RTU | 1 | On | -
DG1-START-CMD | Generator controller DG1 | Start | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG1-STOP-CMD | Generator controller DG1 | Stop | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG1-MODE-CMD | Generator controller DG1 | Mode auto / manual | Write | Command | - | Modbus TCP or RTU | - | - | Admin
DG2-U-L1 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-U-L2 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-U-L3 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-I-L1 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-I-L2 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-I-L3 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-P | Generator controller DG2 | Active power | Read | Measured | kW | Modbus TCP or RTU | - | - | -
DG2-Q | Generator controller DG2 | Reactive power | Read | Measured | kvar | Modbus TCP or RTU | - | - | -
DG2-PF | Generator controller DG2 | Power factor | Read | Measured | - | Modbus TCP or RTU | - | - | -
DG2-F | Generator controller DG2 | Frequency | Read | Measured | Hz | Modbus TCP or RTU | - | - | -
DG2-OIL-P | Generator controller DG2 | Oil pressure | Read | Measured | kPa | Modbus TCP or RTU | - | - | -
DG2-COOL-T | Generator controller DG2 | Coolant temperature | Read | Measured | deg C | Modbus TCP or RTU | - | - | -
DG2-BATT-U | Generator controller DG2 | Starter battery voltage | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-FUEL-COM | Generator controller DG2 | Fuel level | Read | Measured | % | Modbus TCP or RTU | - | - | - | Communicated copy of hardwired signal DG2-FUEL
DG2-HOURS | Generator controller DG2 | Running hours | Read | Counter | h | Modbus TCP or RTU | - | - | -
DG2-STARTS | Generator controller DG2 | Number of starts | Read | Counter | - | Modbus TCP or RTU | - | - | -
DG2-E-TOT | Generator controller DG2 | Energy total | Read | Counter | MWh | Modbus TCP or RTU | - | - | -
DG2-MODE | Generator controller DG2 | Controller mode | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG2-GCB | Generator controller DG2 | Breaker status | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG2-WARN | Generator controller DG2 | Warning | Read | Status | - | Modbus TCP or RTU | 3 | On | -
DG2-SHUTDOWN | Generator controller DG2 | Shutdown alarm | Read | Status | - | Modbus TCP or RTU | 1 | On | -
DG2-START-CMD | Generator controller DG2 | Start | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG2-STOP-CMD | Generator controller DG2 | Stop | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG2-MODE-CMD | Generator controller DG2 | Mode auto / manual | Write | Command | - | Modbus TCP or RTU | - | - | Admin
AH1-I-L1 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-L2 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-L3 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-E | 11 kV protection relay AH1 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L1 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L2 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L3 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-P | 11 kV protection relay AH1 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH1-Q | 11 kV protection relay AH1 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH1-PF | 11 kV protection relay AH1 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH1-F | 11 kV protection relay AH1 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH1-E-IMP | 11 kV protection relay AH1 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH1-E-EXP | 11 kV protection relay AH1 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH1-CB-POS | 11 kV protection relay AH1 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH1-TRIP-50 | 11 kV protection relay AH1 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-50N | 11 kV protection relay AH1 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-27-59 | 11 kV protection relay AH1 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-81 | 11 kV protection relay AH1 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-RLY-HEALTHY | 11 kV protection relay AH1 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH1-DREC | 11 kV protection relay AH1 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH1-TCS-ALM | 11 kV protection relay AH1 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH1-TRIP-51G | 11 kV protection relay AH1 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH1-TRIP-32 | 11 kV protection relay AH1 | Reverse power trip (32), AH1 generator incomer | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Protects the generators against reverse power from PV and battery
AH2-I-L1 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-L2 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-L3 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-E | 11 kV protection relay AH2 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L1 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L2 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L3 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-P | 11 kV protection relay AH2 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH2-Q | 11 kV protection relay AH2 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH2-PF | 11 kV protection relay AH2 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH2-F | 11 kV protection relay AH2 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH2-E-IMP | 11 kV protection relay AH2 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH2-E-EXP | 11 kV protection relay AH2 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH2-CB-POS | 11 kV protection relay AH2 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH2-TRIP-50 | 11 kV protection relay AH2 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-50N | 11 kV protection relay AH2 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-27-59 | 11 kV protection relay AH2 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-81 | 11 kV protection relay AH2 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-RLY-HEALTHY | 11 kV protection relay AH2 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH2-DREC | 11 kV protection relay AH2 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH2-TCS-ALM | 11 kV protection relay AH2 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH2-TRIP-51G | 11 kV protection relay AH2 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH3-I-L1 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-L2 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-L3 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-E | 11 kV protection relay AH3 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L1 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L2 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L3 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-P | 11 kV protection relay AH3 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH3-Q | 11 kV protection relay AH3 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH3-PF | 11 kV protection relay AH3 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH3-F | 11 kV protection relay AH3 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH3-E-IMP | 11 kV protection relay AH3 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH3-E-EXP | 11 kV protection relay AH3 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH3-CB-POS | 11 kV protection relay AH3 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH3-TRIP-50 | 11 kV protection relay AH3 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-50N | 11 kV protection relay AH3 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-27-59 | 11 kV protection relay AH3 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-81 | 11 kV protection relay AH3 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-RLY-HEALTHY | 11 kV protection relay AH3 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH3-DREC | 11 kV protection relay AH3 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH3-TCS-ALM | 11 kV protection relay AH3 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH3-TRIP-51G | 11 kV protection relay AH3 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH4-I-L1 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-L2 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-L3 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-E | 11 kV protection relay AH4 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L1 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L2 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L3 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-P | 11 kV protection relay AH4 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH4-Q | 11 kV protection relay AH4 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH4-PF | 11 kV protection relay AH4 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH4-F | 11 kV protection relay AH4 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH4-E-IMP | 11 kV protection relay AH4 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH4-E-EXP | 11 kV protection relay AH4 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH4-CB-POS | 11 kV protection relay AH4 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH4-TRIP-50 | 11 kV protection relay AH4 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-50N | 11 kV protection relay AH4 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-27-59 | 11 kV protection relay AH4 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-81 | 11 kV protection relay AH4 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-RLY-HEALTHY | 11 kV protection relay AH4 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH4-DREC | 11 kV protection relay AH4 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH4-TCS-ALM | 11 kV protection relay AH4 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH4-TRIP-51G | 11 kV protection relay AH4 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH5-I-L1 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-L2 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-L3 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-E | 11 kV protection relay AH5 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L1 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L2 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L3 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-P | 11 kV protection relay AH5 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH5-Q | 11 kV protection relay AH5 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH5-PF | 11 kV protection relay AH5 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH5-F | 11 kV protection relay AH5 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH5-E-IMP | 11 kV protection relay AH5 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH5-E-EXP | 11 kV protection relay AH5 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH5-CB-POS | 11 kV protection relay AH5 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH5-TRIP-50 | 11 kV protection relay AH5 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-50N | 11 kV protection relay AH5 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-27-59 | 11 kV protection relay AH5 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-81 | 11 kV protection relay AH5 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-RLY-HEALTHY | 11 kV protection relay AH5 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH5-DREC | 11 kV protection relay AH5 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH5-TCS-ALM | 11 kV protection relay AH5 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH6-I-L1 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-L2 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-L3 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-E | 11 kV protection relay AH6 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L1 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L2 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L3 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-P | 11 kV protection relay AH6 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH6-Q | 11 kV protection relay AH6 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH6-PF | 11 kV protection relay AH6 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH6-F | 11 kV protection relay AH6 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH6-E-IMP | 11 kV protection relay AH6 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH6-E-EXP | 11 kV protection relay AH6 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH6-CB-POS | 11 kV protection relay AH6 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH6-TRIP-50 | 11 kV protection relay AH6 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-50N | 11 kV protection relay AH6 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-27-59 | 11 kV protection relay AH6 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-81 | 11 kV protection relay AH6 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-RLY-HEALTHY | 11 kV protection relay AH6 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH6-DREC | 11 kV protection relay AH6 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH6-TCS-ALM | 11 kV protection relay AH6 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH6-TRIP-51G | 11 kV protection relay AH6 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH7-I-L1 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-L2 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-L3 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-E | 11 kV protection relay AH7 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L1 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L2 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L3 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-P | 11 kV protection relay AH7 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH7-Q | 11 kV protection relay AH7 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH7-PF | 11 kV protection relay AH7 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH7-F | 11 kV protection relay AH7 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH7-E-IMP | 11 kV protection relay AH7 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH7-E-EXP | 11 kV protection relay AH7 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH7-CB-POS | 11 kV protection relay AH7 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH7-TRIP-50 | 11 kV protection relay AH7 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-50N | 11 kV protection relay AH7 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-27-59 | 11 kV protection relay AH7 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-81 | 11 kV protection relay AH7 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-RLY-HEALTHY | 11 kV protection relay AH7 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH7-DREC | 11 kV protection relay AH7 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH7-TCS-ALM | 11 kV protection relay AH7 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH7-TRIP-51G | 11 kV protection relay AH7 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
PRS-RLY-I-L1 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PRS-RLY-I-L2 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PRS-RLY-I-L3 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PRS-RLY-I-E | RMU relay ST260E | Earth current | Read | Measured | A | Modbus RTU through MGate | - | - | -
PRS-RLY-CB-POS | RMU relay ST260E | Breaker position | Read | Double point | - | Modbus RTU through MGate | Status | - | -
PRS-RLY-TRIP-50 | RMU relay ST260E | Overcurrent trip | Read | Event | - | Modbus RTU through MGate | 1 | On | -
PRS-RLY-TRIP-50N | RMU relay ST260E | Earth fault trip | Read | Event | - | Modbus RTU through MGate | 1 | On | -
PRS-RLY-HEALTHY | RMU relay ST260E | Relay healthy | Read | Status | - | Modbus RTU through MGate | 2 | Off | -
PMS-RLY-I-L1 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PMS-RLY-I-L2 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PMS-RLY-I-L3 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PMS-RLY-I-E | RMU relay ST260E | Earth current | Read | Measured | A | Modbus RTU through MGate | - | - | -
PMS-RLY-CB-POS | RMU relay ST260E | Breaker position | Read | Double point | - | Modbus RTU through MGate | Status | - | -
PMS-RLY-TRIP-50 | RMU relay ST260E | Overcurrent trip | Read | Event | - | Modbus RTU through MGate | 1 | On | -
PMS-RLY-TRIP-50N | RMU relay ST260E | Earth fault trip | Read | Event | - | Modbus RTU through MGate | 1 | On | -
PMS-RLY-HEALTHY | RMU relay ST260E | Relay healthy | Read | Status | - | Modbus RTU through MGate | 2 | Off | -
PRS-LV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
PRS-LV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
PRS-LV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
PRS-LV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
PRS-LV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
PRS-LV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
PRS-LV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
PRS-LV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
PRS-LV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
PMS-LV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
PMS-LV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
PMS-LV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
PMS-LV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
PMS-LV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
PMS-LV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
PMS-LV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
PMS-LV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
PMS-LV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
AUXLV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
AUXLV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
AUXLV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
AUXLV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
AUXLV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
AUXLV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
AUXLV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
AUXLV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
AUXLV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
WS-IRR-POA | Weather logger blue'Log XM | Plane-of-array irradiance | Read | Measured | W/m2 | Modbus TCP | - | - | -
WS-WIND-SPD | Weather logger blue'Log XM | Wind speed | Read | Measured | m/s | Modbus TCP | - | - | -
WS-WIND-DIR | Weather logger blue'Log XM | Wind direction | Read | Measured | deg | Modbus TCP | - | - | -
WS-T-AMB | Weather logger blue'Log XM | Ambient temperature | Read | Measured | deg C | Modbus TCP | - | - | -
WS-T-MOD | Weather logger blue'Log XM | Module temperature | Read | Measured | deg C | Modbus TCP | - | - | -
WS-HEALTHY | Weather logger blue'Log XM | Logger healthy | Read | Status | - | Modbus TCP | 2 | Off | -
UPS-U-IN | UPS | Input voltage | Read | Measured | V | Modbus TCP or SNMP | - | - | -
UPS-LOAD | UPS | Output load | Read | Measured | % | Modbus TCP or SNMP | - | - | -
UPS-BATT-CHG | UPS | Battery charge | Read | Measured | % | Modbus TCP or SNMP | - | - | -
UPS-RUNTIME | UPS | Runtime remaining | Read | Measured | min | Modbus TCP or SNMP | - | - | -
UPS-ON-BATT-COM | UPS | On battery | Read | Status | - | Modbus TCP or SNMP | 2 | On | - | Communicated copy of hardwired signal UPS-ON-BATT
UPS-FLT-COM | UPS | Fault | Read | Status | - | Modbus TCP or SNMP | 2 | On | - | Communicated copy of hardwired signal UPS-FLT
SW-CORE-A-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-A-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-B-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-B-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-MV-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-MV-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-BESS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-BESS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-GEN-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-GEN-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PRS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PRS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PMS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PMS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
FW-HEALTHY | Firewall and GPS time server | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
FW-VPN-ACTIVE | Firewall and GPS time server | Time synchronised / VPN session active | Read | Status | - | SNMP v3 | 3 | On | -
GPS-HEALTHY | Firewall and GPS time server | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
GPS-TIME-SYNC | Firewall and GPS time server | Time synchronised / VPN session active | Read | Status | - | SNMP v3 | 3 | Off | -
PLCBOX-NB01-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB02-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB03-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB04-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
CP-A-HEALTHY | SICAM CP-8050 A | Controller A healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-A-PS1-OK | SICAM CP-8050 A | Controller A power supply 1 healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-A-PS2-OK | SICAM CP-8050 A | Controller A power supply 2 healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-A-ACTIVE | SICAM CP-8050 A | Controller A active | Read | Status | - | Internal | Status | - | - | Added rev 1. Shows which controller is in control
CP-B-HEALTHY | SICAM CP-8050 B | Controller B healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-B-PS1-OK | SICAM CP-8050 B | Controller B power supply 1 healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-B-PS2-OK | SICAM CP-8050 B | Controller B power supply 2 healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. One per controller of the hot standby pair
CP-B-ACTIVE | SICAM CP-8050 B | Controller B active | Read | Status | - | Internal | Status | - | - | Added rev 1. Shows which controller is in control
CP-ROW1-OK | SICAM CP-8050 internal | I/O row 1 link healthy | Read | Status | - | Internal | 2 | Off | - | Added rev 1. Row 1 now has its own CI-8532 interface, so both controllers reach it
CP-ROW2-OK | SICAM CP-8050 internal | I/O row 2 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW3-OK | SICAM CP-8050 internal | I/O row 3 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW4-OK | SICAM CP-8050 internal | I/O row 4 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW5-OK | SICAM CP-8050 internal | I/O row 5 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW6-OK | SICAM CP-8050 internal | I/O row 6 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-LINK1-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK2-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK3-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK4-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK5-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK6-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK7-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK8-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-REDUN-OK | SICAM CP-8050 internal | Standby controller synchronised and ready | Read | Status | - | Internal | 2 | Off | - | Added rev 1. Off means a failure of the active controller would not be covered
CP-SWITCHOVER | SICAM CP-8050 internal | Controller switchover occurred | Read | Event | - | Internal | 3 | On | - | Added rev 1. Logged with time; resets on acknowledgement

## Datasheets
No. | Group | Item | Manufacturer | Model | Order no. to search | Documents to collect | Where to download | Collected
1 | Controller | Processor module | Siemens | SICAM A8000 CP-8050 | 6MF2805-0AA00 | Datasheet; CP-8050 system manual; redundancy description; security manual | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
2 | Controller | Power supply | Siemens | SICAM A8000 PS-8642 | 6MF2864-2AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
3 | Controller | Ethernet interface | Siemens | SICAM A8000 CI-8520 | 6MF2852-0AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
4 | Controller | Flash card | Siemens | SICAM flash card 2 GB | 6MF1213-1GA05-0AA0 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
5 | I/O | Digital input module | Siemens | SICAM A8000 DI-8112 | 6MF2811-2AA00 | Datasheet (confirm input voltage) | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
6 | I/O | Secured command output | Siemens | SICAM A8000 DO-8221 | Ask Siemens | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
7 | I/O | Relay output module | Siemens | SICAM A8000 DO-8212 | 6MF2821-2AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
8 | I/O | Analogue input module | Siemens | SICAM A8000 AI-8320 | 6MF2832-0AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
9 | I/O | Remote interface, electrical | Siemens | SICAM A8000 CI-8532 | 6MF2853-2AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
10 | I/O | Remote interface, optical | Siemens | SICAM A8000 CI-8533 | Ask Siemens | Datasheet, incl. fibre type and maximum length | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
11 | I/O | SICAM A8000 series | Siemens | SICAM A8000 catalogue | - | Catalogue / module overview | Siemens SICAM A8000 product page (siemens.com, search 'SICAM A8000')
12 | SCADA | SCADA servers | Siemens | SIMATIC IPC647E | Configured order no. | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
13 | SCADA | Operator workstation | Dell | OptiPlex 7000 series | Configured | Specification sheet | dell.com, product page 'OptiPlex 7000', Specifications
14 | SCADA | Engineering laptop | Dell | Latitude 5430 Rugged | Configured | Specification sheet | dell.com, product page 'Latitude 5430 Rugged', Specifications
15 | Network | Core switches | Siemens or Moxa | SCALANCE XC216-4C (or Moxa EDS-G512E) | Per final choice | Datasheet; substation rating if any | SIOS for SCALANCE; moxa.com product page for Moxa
16 | Network | Field and station switches | Siemens or Moxa | SCALANCE XC208 / XC206-2SFP EEC (or Moxa EDS-510E) | Per final choice | Datasheet | SIOS for SCALANCE; moxa.com product page for Moxa
17 | Network | Fibre transceivers | Siemens or Moxa | SCALANCE SFP992-1LD (or Moxa SFP-1GLXLC) | Per final choice | Datasheet | SIOS for SCALANCE; moxa.com product page for Moxa
18 | Network | Serial gateway for RMU relays | Moxa (or Siemens RUGGEDCOM) | MGate MB3170 (or RUGGEDCOM RS416 / RMC30) | Per final choice | Datasheet | moxa.com product page; or siemens.com RUGGEDCOM pages
19 | Network | Firewall and VPN | Siemens or Fortinet | SCALANCE SC646-2C (or FortiGate Rugged 60F) | Per final choice | Datasheet | SIOS for SCALANCE; fortinet.com data sheets library for FortiGate Rugged
20 | Network | GPS time server | Meinberg | LANTIME M300/GPS | M300/GPS | Datasheet | meinbergglobal.com, product page LANTIME M300
21 | Power | Power meters | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | Datasheet; Modbus register list | se.com, search 'METSEPM5560', Documents
22 | Power | 24 V DC power supplies | Siemens | SITOP PSU8200 24 V/20 A | 6EP1336-3BA10 | Datasheet; SITOP PSU8200 1-phase manual | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
23 | Power | UPS | APC (Schneider Electric) | Smart-UPS SRT 3000 VA | SRT3000RMXLI | Datasheet | apc.com or se.com, search 'SRT3000RMXLI'
24 | Enclosure | SCADA cabinet | Rittal | VX25 800 x 2000 x 800 | 8808.000 | Datasheet | rittal.com, search '8808.000'
25 | Enclosure | Outdoor I/O panels | Rittal | AX, size to suit | Per size | Datasheet | rittal.com, AX compact enclosures
26 | Enclosure | Alarm sounder and beacon | Pfannenberg | PATROL series | Per model | Datasheet | pfannenberg.com, PATROL series
27 | Software | Substation SCADA | Siemens | SICAM SCC | Per licence quote | Product description; system requirements; licensing | Siemens SICAM SCC product page; documents via SIOS
28 | Software | Controller engineering tool | Siemens | SICAM Device Manager | Per licence quote | Product information; system requirements | Siemens SICAM A8000 / Device Manager pages; SIOS
29 | Software | Network management | Siemens or Moxa | SINEC NMS (or Moxa MXview One) | Per licence quote | Product information | SIOS for SINEC NMS; moxa.com for MXview One
30 | Software | Remote access management | Siemens or Fortinet | SINEMA Remote Connect (or FortiClient) | Per licence quote | Product information | SIOS for SINEMA RC; fortinet.com for FortiClient
31 | Software | Operating systems | Microsoft | Windows Server, Windows 11 Pro | - | Not usually requested; licence certificates at delivery | -
32 | Field device | PV inverters | Sungrow | SG350HX | - | Datasheet; communication protocol | sungrowpower.com product page; or PV designer
33 | Field device | Power line communication box | Sungrow | TBC | - | Datasheet; Modbus point table | PV designer
34 | Field device | Battery system | Sungrow | ST3340UX | - | Datasheet; communication protocol | Battery supplier
35 | Field device | Embedded EMS | TBC | TBC | - | Datasheet; Modbus point table | PV designer
36 | Field device | Generator controllers | TBC | TBC | - | Datasheet; Modbus point table | Generator supplier
37 | Field device | 11 kV protection relays | TBC | TBC | - | Datasheet; IEC 61850 or Modbus documentation | Switchgear supplier
38 | Field device | RMU relays | Per RMU supplier | ST260E | - | Datasheet; Modbus map | RMU supplier
39 | Field device | Fire detection and suppression panel | TBC | TBC | - | Datasheet; contact schedule | Fire system supplier
40 | Field device | Weather logger | Meteocontrol | blue'Log XM | - | Datasheet; Modbus documentation | meteocontrol.com product page
41 | Field device | Pyranometer | Kipp & Zonen | SMP12-A | - | Datasheet | kippzonen.com / otthydromet.com product page
42 | Field device | Wind sensor | Gill Instruments | WindSonic RS485 | - | Datasheet | gillinstruments.com product page
Fill the Collected column as each file is saved. Name files '<No.>_<Model>.pdf' so they sort in this order inside the zip.
Network items list both Siemens SCALANCE and Moxa/Fortinet; collect only the final choice.