## Read Me
Villa Somalia Hybrid Plant: SCADA Device and I/O List
Project | Solarization of Villa Somalia, Mogadishu. 1,516 kWp PV, 3,340 kWh BESS, 2 diesel generators, 11 kV switchboard, 2 office transformer stations.
Status | Rev 1, 15 Oct 2026: harmonised with the design report, the drawings and the HMI demonstration. For client submission as Attachment B.
Controller | Siemens SICAM A8000 CP-8050 as plant controller and gateway. The embedded EMS keeps dispatch of PV, battery and generators.
SCADA | Siemens SICAM SCC on two servers (active and hot standby), linked to the CP-8050 by IEC 60870-5-104.
Sheets
Device List | Every device in the design: model, product or ordering number, quantity, location, interface and protocol to the CP-8050.
Protocol Summary | Device quantities per protocol, calculated from the Device List.
IO List | Every hardwired signal: tag, description, type, I/O row, module and channel, alarm level and who may operate it.
Datasheets | Register of every datasheet and software document for Attachment C, with where to download it and a Collected column.
IO Rows | Where each of the six I/O rows sits, its remote interface, link to the CP-8050 and the equipment wired to it.
IO Summary | Channels used and spare per I/O module, calculated from the IO List.
Comms Points | Typical signals read or written over communication links, per device type, with quantities. Replace with each vendor's point table.
Comms Point List | The Comms Points expanded to one row per signal, each with its own tag and alarm level, as used by the HMI.
Number status key
Checked | Product number found on a supplier listing or a Siemens configuration document.
From memory - confirm | Ordering code from knowledge of the maker's catalogue; not checked online. Confirm with the distributor.
To confirm with supplier | Product exists but its number was not found. Take it from the supplier's quotation.
Existing (drawings) | Device already specified in drawing set VILLA_SOMALIA_05_10_2026.
TBC | Make or model unknown. Must come from the PV designer or the equipment supplier. Cells marked TBC are shaded yellow.
Assumptions
1 | Auxiliary control voltage is 110 V DC. This selects DI-8112, CI-8532, CI-8533 and PS-8642. For 24 V or 220 V DC see the variant note on the Device List.
2 | 11 kV breakers, RMU switches and LVDB incomers are motorised and accept remote open and close.
3 | The embedded EMS offers Modbus TCP. The PV inverter data reaches the CP-8050 from the power line communication box, as shown on the existing communication sheet.
4 | Signal counts per device are typical values. They must be checked against the switchgear, RMU, transformer and fire panel terminal schedules.
5 | Measurements (current, voltage, power, energy) come over communication from relays, meters and the EMS, not hardwired.
6 | Spare capacity target is about 20% per I/O row.
7 | Field signals are collected by the nearest I/O row: switchroom (rows 1, 2), office stations (rows 3, 4), BESS and inverter transformer yard (row 5), generator area (row 6). Remote rows 3 to 6 link to the CP-8050 by fibre. Actual cable distances are not known yet.
Revision 1 changes
1 | AH8: breaker open, closed, tripped, earth switch and gas pressure added (row 1). The 11 kV system is earthed only through AH8.
2 | LV main breakers added: PV ACB 1250 A and BESS ACB 1000 A (row 5), DG step-up transformer LV ACB (row 6).
3 | Combiner panels: trip of the four inverter AC MCCBs (row 5); battery combiner panel switch and fuse status through the EMS.
4 | Auxiliary transformer XRNT-3A fuse blown (row 2); RMU UPS 2 kVA on battery and fault at both office stations (rows 3, 4).
5 | 11 kV relays: trip circuit supervision (7), sensitive earth fault trip (6) and reverse power trip on AH1 added as communication points.
6 | Totals: 244 hardwired signals and 456 communication points. Overall spare is 27%; row 5 drops to 19% (6 of 32 channels), just under the 20% target: add a third DI-8112 there if more yard signals appear.
7 | Comms Point List sheet added. Devices D49 and D50 added to the Device List.

## Device List
ID | Group | Device | Manufacturer | Model | Product / ordering no. | Number status | Qty | Location | Physical interface | Protocol to CP-8050 | Primary protocol | Hardwired to I/O row | Notes
A. Plant equipment (existing or by others)
D01 | Plant | PV string inverters NB01 to NB04 | Sungrow | SG350HX | - | Existing (drawings) | 4 | PV field | AC power cable | Power line communication to the PLC box | Power line communication | - | Not connected to the CP-8050 directly.
D02 | Plant | Power line communication box (PLC box) | Sungrow | TBC | TBC | TBC | 1 | Inverter MV station | Ethernet RJ45 | Modbus TCP (to confirm) | Modbus TCP | - | Converts inverter data to Ethernet. Get model and point table from the PV designer.
D03 | Plant | Embedded energy management system (EMS) | TBC | TBC | TBC | TBC | 1 | BESS / EMS area | Ethernet RJ45 | Modbus TCP (to confirm) | Modbus TCP | - | Dispatches PV, battery and generators. Only the CP-8050 writes settings to it.
D04 | Plant | Battery energy storage system, 3,340 kWh | Sungrow | ST3340UX | - | Existing (drawings) | 1 | BESS area | Ethernet (via EMS) | Through the EMS, Modbus TCP | Modbus TCP | - | Confirm whether battery data is read through the EMS or directly. Battery combiner panel status read through the EMS if available (rev 1).
D05 | Plant | Generator controllers DG1, DG2 | TBC | TBC | TBC | TBC | 2 | Generator area | Ethernet or RS485 | Modbus TCP, or Modbus RTU through a gateway | Modbus TCP | Row 6 | Breaker status, alarm, E-stop, running and fuel level also hardwired to row 6.
D06 | Plant | 11 kV protection relays, panels AH1 to AH7 | TBC (switchgear supplier) | TBC | TBC | TBC | 7 | 11 kV switchroom | Ethernet, 2 ports preferred | IEC 61850 MMS, or Modbus TCP | IEC 61850 | Row 1 | Dual-connect to both core switches if the relay has two ports.
D07 | Plant | Neutral earthing resistor panel AH8 | TBC (switchgear supplier) | - | - | TBC | 1 | 11 kV switchroom | Dry contacts | Hardwired | Hardwired | Row 1 | Breaker position, trip, earth switch and gas pressure also wired to row 1 (rev 1).
D08 | Plant | RMU protection relays | Per RMU supplier | ST260E | - | Existing (drawings) | 2 | President and PM stations | RS485 | Modbus RTU, converted by MGate gateway | Modbus RTU | Rows 3, 4 | Confirm Modbus map with the RMU supplier.
D09 | Plant | Transformers: inverter, DG step-up, 100 kVA auxiliary | TBC | - | - | TBC | 3 | Yard, generator area, switchroom | Dry contacts | Hardwired | Hardwired | Rows 5, 6, 2 | Each wired to the nearest I/O row: inverter to row 5, DG step-up to row 6, auxiliary to row 2. Auxiliary transformer also has its XRNT-3A fuse striker wired to row 2 (rev 1).
D10 | Plant | Transformers 630 kVA, President and PM stations | TBC | - | - | TBC | 2 | Office stations | Dry contacts | Hardwired | Hardwired | Rows 3, 4
D11 | Plant | Low-voltage distribution boards, 10-way | TBC | - | - | TBC | 2 | Office stations | Dry contacts + meter | Hardwired; meter on Modbus TCP | Hardwired | Rows 3, 4
D12 | Plant | Fire detection and suppression panel | TBC | TBC | TBC | TBC | 1 | BESS area | Dry contacts | Hardwired | Hardwired | Row 5 | Also a direct hardwired trip to the battery, outside the SCADA.
D13 | Plant | UPS and auxiliary DC supplies | TBC | TBC | TBC | TBC | 1 | 11 kV switchroom | Ethernet or dry contacts | Modbus TCP or SNMP, plus contacts | Modbus TCP | Row 2
D14 | Plant | Weather station data logger | Meteocontrol | blue'Log XM with Multi I/O and Fieldbus Ext | - | Existing (drawings) | 1 | Inverter MV station | Ethernet RJ45 | Modbus TCP | Modbus TCP | - | Collects the sensors below.
D15 | Plant | Pyranometer | Kipp & Zonen | SMP12-A | - | Existing (drawings) | 1 | Weather mast | RS485 to logger | Through the blue'Log | Through logger | -
D16 | Plant | Wind sensor | Gill Instruments | WindSonic RS485 | - | Existing (drawings) | 1 | Weather mast | RS485 to logger | Through the blue'Log | Through logger | -
D17 | Plant | Ambient and module temperature sensors | TBC | - | - | Existing (drawings) | 2 | Weather mast / PV array | Analogue to logger | Through the blue'Log | Through logger | -
D49 | Plant | LV main breakers: PV ACB 1250 A, BESS ACB 1000 A, DG step-up LV ACB; inverter AC MCCBs 400 A | TBC (switchboard supplier) | - | - | Existing (drawings) | 3 | Inverter MV station, BESS area, generator area | Dry contacts | Hardwired | Hardwired | Rows 5, 6 | Added rev 1. Position and trip of each main breaker; trip of the four inverter MCCBs (row 5).
D50 | Plant | RMU UPS 2 kVA, 220 V AC | TBC (RMU supplier) | - | - | Existing (drawings) | 2 | President and PM stations | Dry contacts | Hardwired | Hardwired | Rows 3, 4 | Added rev 1. On battery and fault contacts.
B. SICAM A8000 controller and I/O
D18 | Controller | Processor module | Siemens | CP-8050 | 6MF2805-0AA00 | Checked | 1 | 11 kV switchroom | 2 x RJ45 | Gateway for all protocols | IEC 60870-5-104 | - | To SCADA servers A and B.
D19 | Controller | Power supply, 100 to 240 V DC/AC, 45 W | Siemens | PS-8642 | 6MF2864-2AA00 | Checked | 2 | 11 kV switchroom | - | - | N/A | - | Two for redundancy; confirm the CP-8050 supports a second supply.
D20 | Controller | Ethernet interface, 5 x RJ45 | Siemens | CI-8520 | 6MF2852-0AA00 | Checked | 1 | 11 kV switchroom | 5 x RJ45 | Separate ports per network zone | N/A | - | Not a managed switch.
D21 | Controller | Flash card, 2 GB | Siemens | SICAM flash card | 6MF1213-1GA05-0AA0 | Checked | 1 | 11 kV switchroom | - | - | N/A | -
D22 | I/O | Digital input, 2 x 8 inputs | Siemens | DI-8112 | 6MF2811-2AA00 | Checked | 17 | Rows 1 to 6 | Terminal | SICAM I/O link | SICAM I/O link | Rows 1-6 | Confirm DI-8112 is the 110 V DC variant. 24 V: DI-8110, 6MF2811-0AA00. 220 V: DI-8113, 6MF2811-3AA00.
D23 | I/O | Secured command output, 12 outputs | Siemens | DO-8221 | To confirm | To confirm with supplier | 4 | Rows 1, 3, 4 | Terminal | SICAM I/O link | SICAM I/O link | Rows 1, 3, 4 | Breaker open and close with 1-out-of-n check.
D24 | I/O | Digital output, 8 relays, 24-220 V DC / 230 V AC | Siemens | DO-8212 | 6MF2821-2AA00 | Checked | 1 | Row 1 | Terminal | SICAM I/O link | SICAM I/O link | Row 1 | Alarm beacon and controller healthy output.
D25 | I/O | Analogue input, 4 x +/-20 mA or +/-10 V | Siemens | AI-8320 | 6MF2832-0AA00 | Checked | 2 | Rows 2, 6 | Terminal | SICAM I/O link | SICAM I/O link | Rows 2, 6 | Row 2: DC bus voltages. Row 6: generator fuel levels.
D26 | I/O | I/O remote interface, electrical, 110-220 V DC | Siemens | CI-8532 | 6MF2853-2AA00 | Checked | 1 | Row 2 | Copper | SICAM I/O link | SICAM I/O link | Row 2 | 24 V variant: CI-8530, 6MF2853-0AA00.
D27 | I/O | I/O remote interface, optical, 110-220 V DC | Siemens | CI-8533 | To confirm | To confirm with supplier | 4 | Rows 3 to 6 | Fibre | SICAM I/O link, optical | SICAM I/O link | Rows 3-6 | One per remote row: President, Prime Minister, BESS yard, generator area. Confirm fibre type and maximum length. Within about 100 m of the switchroom, CI-8532 on copper may be used instead. 24 V variant: CI-8531.
D28 | I/O | Protocol licences: IEC 104, Modbus TCP client, IEC 61850 client | Siemens | For CP-8050 | By quotation | To confirm with supplier | 1 | - | - | - | N/A | -
C. Network, time and security
D29 | Network | Core switch, managed, gigabit, SFP | Moxa | EDS-G512E | EDS-G512E-4GSFP | From memory - confirm | 2 | 11 kV switchroom | RJ45 + SFP | Ethernet, VLANs, ring | N/A | - | Core switch A and B.
D30 | Network | Field and station switch, managed, SFP | Moxa | EDS-510E | EDS-510E-3GTXSFP | From memory - confirm | 5 | MV station, BESS, generators, 2 office stations | RJ45 + SFP | Ethernet, ring | N/A | - | Replaces the unmanaged switch on the existing sheet.
D31 | Network | Fibre transceiver, single-mode, gigabit | Moxa | SFP-1GLXLC | SFP-1GLXLC | From memory - confirm | 14 | All switches | LC fibre | - | N/A | - | 7-switch ring, 2 per link.
D32 | Network | Serial to Ethernet gateway | Moxa | MGate MB3170 | MB3170 | From memory - confirm | 2 | Office stations | RS485 + RJ45 | Modbus RTU to Modbus TCP | Modbus TCP | - | Add one more if the generator controllers are RS485 only.
D33 | Network | Firewall with VPN | Fortinet | FortiGate Rugged 60F | FGR-60F | From memory - confirm | 1 | 11 kV switchroom | RJ45 | VPN, off by default | N/A | - | Second unit optional.
D34 | Network | GPS time server with antenna | Meinberg | LANTIME M300 | M300/GPS | From memory - confirm | 1 | 11 kV switchroom | RJ45 | NTP | NTP | -
D35 | Network | Armoured single-mode fibre, 12 core, with patch panels | To suit | - | Length per route | TBC | 3 | Switchroom-President, switchroom-PM, President-PM | LC | - | N/A | - | Third route closes the ring. Rows 5 and 6 use spare cores in the fibre cables to field switches 2 and 3.
D. SCADA computers, power and enclosures
D36 | SCADA | SCADA server, rack industrial PC | Siemens | SIMATIC IPC647E | Configured to order | To confirm with supplier | 2 | Control room | 2 x RJ45 | IEC 60870-5-104 | IEC 60870-5-104 | - | Server A active, server B hot standby.
D37 | SCADA | Operator workstation with two 24-inch monitors | Dell | OptiPlex 7000 series | Configured to order | To confirm with supplier | 1 | Control room | RJ45 | - | N/A | -
D38 | SCADA | Engineering laptop | Dell | Latitude 5430 Rugged | Configured to order | To confirm with supplier | 1 | Control room | RJ45 | - | N/A | -
D39 | SCADA | Power meter | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | From memory - confirm | 3 | LVDB President, LVDB PM, auxiliary board | RJ45 | Modbus TCP | Modbus TCP | -
D40 | SCADA | 24 V DC power supply, 20 A, 1-phase | Siemens | SITOP PSU8200 24 V/20 A | 6EP1336-3BA10 | Checked | 6 | Switchroom, office stations, BESS yard, generator area | - | - | N/A | - | Switches and gateways. Input 85-275 V AC or 88-350 V DC, so it can run from the 110 V DC station battery. Add SITOP UPS1600 if 24 V must ride through loss of input.
D41 | SCADA | UPS for the SCADA cabinet, 3000 VA | APC | Smart-UPS SRT 3000 | SRT3000RMXLI | From memory - confirm | 1 | Control room | RJ45 | SNMP | N/A | - | About 2 hours runtime with battery pack; size at design.
D42 | SCADA | SCADA cabinet, 800 x 2000 x 800 mm | Rittal | VX25 | 8808.000 | From memory - confirm | 1 | 11 kV switchroom | - | - | N/A | Row 2 | Door contact wired to row 2.
D43 | SCADA | Outdoor I/O panel, IP55 minimum | Rittal | AX | Size to suit | TBC | 4 | Office stations, BESS yard, generator area | - | - | N/A | Rows 3-6 | Shaded or air-conditioned where exposed to direct sun.
D44 | SCADA | Alarm sounder and beacon | Pfannenberg | PATROL | Model to suit | TBC | 1 | Control room | Terminal | Hardwired | Hardwired | Row 1
E. Software
D45 | Software | Substation SCADA, redundant | Siemens | SICAM SCC | By quotation | To confirm with supplier | 1 | SCADA servers | - | IEC 60870-5-104 | N/A | - | Licence sized for about 700 signals; includes Operator and Admin roles.
D46 | Software | Controller engineering tool | Siemens | SICAM Device Manager | By quotation | To confirm with supplier | 1 | Engineering laptop | - | - | N/A | -
D47 | Software | Network management | Moxa | MXview One | By quotation | To confirm with supplier | 1 | SCADA server | - | SNMP | N/A | -
D48 | Software | VPN client | Fortinet | FortiClient | - | - | 1 | Remote users | - | - | N/A | -

## Protocol Summary
Primary protocol | Where used | Device lines | Device quantity
IEC 60870-5-104 | CP-8050 to SCADA servers A and B
IEC 61850 | 11 kV protection relays (Modbus TCP if not supported)
Modbus TCP | PLC box, EMS, battery via EMS, generator controllers, power meters, weather logger, UPS, gateways
Modbus RTU | RMU relays ST260E, through MGate gateways
SICAM I/O link | CP-8050 to I/O modules and remote rows (Siemens proprietary)
Hardwired | Status contacts, alarms and commands wired to I/O modules
Power line communication | PV inverters to the PLC box over the AC cables
NTP | Time synchronisation from the GPS time server
Through logger | Weather sensors to the blue'Log
Supervision protocols: SNMP v3 and syslog from switches, firewall and time server to the SCADA servers.

## IO List
Tag | Description | Equipment | Location | Type | I/O row | Module | Module type | Channel | Normal state / range | Alarm level | Operated by | Notes
AH1-CB-OPEN | Circuit breaker open | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 1 | Status | Status | -
AH1-CB-CLSD | Circuit breaker closed | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 2 | Status | Status | -
AH1-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 3 | Normally open | 1 | -
AH1-ES-CLSD | Earth switch closed | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 4 | Status | Status | - | Interlock: blocks remote close
AH1-LR-REM | Local/remote switch in remote | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 5 | Status | Status | - | Interlock: remote commands only in remote
AH1-SPR-CHG | Closing spring charged | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 6 | Normally closed | 3 | -
AH1-GAS-LOW | Gas pressure low | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 7 | Normally open | 2 | -
AH1-RLY-OK | Protection relay healthy | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 8 | Normally closed | 2 | -
AH1-AUX-OK | Control supply healthy | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 9 | Normally closed | 2 | -
AH2-CB-OPEN | Circuit breaker open | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 10 | Status | Status | -
AH2-CB-CLSD | Circuit breaker closed | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 11 | Status | Status | -
AH2-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 12 | Normally open | 1 | -
AH2-ES-CLSD | Earth switch closed | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 13 | Status | Status | - | Interlock: blocks remote close
AH2-LR-REM | Local/remote switch in remote | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 14 | Status | Status | - | Interlock: remote commands only in remote
AH2-SPR-CHG | Closing spring charged | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 15 | Normally closed | 3 | -
AH2-GAS-LOW | Gas pressure low | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI01 | DI-8112 | 16 | Normally open | 2 | -
AH2-RLY-OK | Protection relay healthy | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 1 | Normally closed | 2 | -
AH2-AUX-OK | Control supply healthy | 11 kV panel AH2, PV incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 2 | Normally closed | 2 | -
AH3-CB-OPEN | Circuit breaker open | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 3 | Status | Status | -
AH3-CB-CLSD | Circuit breaker closed | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 4 | Status | Status | -
AH3-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 5 | Normally open | 1 | -
AH3-ES-CLSD | Earth switch closed | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 6 | Status | Status | - | Interlock: blocks remote close
AH3-LR-REM | Local/remote switch in remote | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 7 | Status | Status | - | Interlock: remote commands only in remote
AH3-SPR-CHG | Closing spring charged | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 8 | Normally closed | 3 | -
AH3-GAS-LOW | Gas pressure low | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 9 | Normally open | 2 | -
AH3-RLY-OK | Protection relay healthy | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 10 | Normally closed | 2 | -
AH3-AUX-OK | Control supply healthy | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 11 | Normally closed | 2 | -
AH4-CB-OPEN | Circuit breaker open | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 12 | Status | Status | -
AH4-CB-CLSD | Circuit breaker closed | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 13 | Status | Status | -
AH4-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 14 | Normally open | 1 | -
AH4-ES-CLSD | Earth switch closed | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 15 | Status | Status | - | Interlock: blocks remote close
AH4-LR-REM | Local/remote switch in remote | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI02 | DI-8112 | 16 | Status | Status | - | Interlock: remote commands only in remote
AH4-SPR-CHG | Closing spring charged | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 1 | Normally closed | 3 | -
AH4-GAS-LOW | Gas pressure low | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 2 | Normally open | 2 | -
AH4-RLY-OK | Protection relay healthy | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 3 | Normally closed | 2 | -
AH4-AUX-OK | Control supply healthy | 11 kV panel AH4, President feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 4 | Normally closed | 2 | -
AH5-CB-OPEN | Circuit breaker open | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 5 | Status | Status | -
AH5-CB-CLSD | Circuit breaker closed | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 6 | Status | Status | -
AH5-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 7 | Normally open | 1 | -
AH5-ES-CLSD | Earth switch closed | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 8 | Status | Status | - | Interlock: blocks remote close
AH5-LR-REM | Local/remote switch in remote | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 9 | Status | Status | - | Interlock: remote commands only in remote
AH5-SPR-CHG | Closing spring charged | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 10 | Normally closed | 3 | -
AH5-GAS-LOW | Gas pressure low | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 11 | Normally open | 2 | -
AH5-RLY-OK | Protection relay healthy | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 12 | Normally closed | 2 | -
AH5-AUX-OK | Control supply healthy | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 13 | Normally closed | 2 | -
AH6-CB-OPEN | Circuit breaker open | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 14 | Status | Status | -
AH6-CB-CLSD | Circuit breaker closed | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 15 | Status | Status | -
AH6-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI03 | DI-8112 | 16 | Normally open | 1 | -
AH6-ES-CLSD | Earth switch closed | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 1 | Status | Status | - | Interlock: blocks remote close
AH6-LR-REM | Local/remote switch in remote | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 2 | Status | Status | - | Interlock: remote commands only in remote
AH6-SPR-CHG | Closing spring charged | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 3 | Normally closed | 3 | -
AH6-GAS-LOW | Gas pressure low | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 4 | Normally open | 2 | -
AH6-RLY-OK | Protection relay healthy | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 5 | Normally closed | 2 | -
AH6-AUX-OK | Control supply healthy | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 6 | Normally closed | 2 | -
AH7-CB-OPEN | Circuit breaker open | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 7 | Status | Status | -
AH7-CB-CLSD | Circuit breaker closed | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 8 | Status | Status | -
AH7-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 9 | Normally open | 1 | -
AH7-ES-CLSD | Earth switch closed | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 10 | Status | Status | - | Interlock: blocks remote close
AH7-LR-REM | Local/remote switch in remote | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 11 | Status | Status | - | Interlock: remote commands only in remote
AH7-SPR-CHG | Closing spring charged | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 12 | Normally closed | 3 | -
AH7-GAS-LOW | Gas pressure low | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 13 | Normally open | 2 | -
AH7-RLY-OK | Protection relay healthy | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 14 | Normally closed | 2 | -
AH7-AUX-OK | Control supply healthy | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 15 | Normally closed | 2 | -
AH1-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 1 | Pulse | - | Operator | Select then confirm
AH1-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH1, Generator incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH2-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH2, PV incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 3 | Pulse | - | Operator | Select then confirm
AH2-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH2, PV incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH3-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 5 | Pulse | - | Operator | Select then confirm
AH3-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH3, BESS incomer | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH4-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH4, President feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 7 | Pulse | - | Operator | Select then confirm
AH4-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH4, President feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 8 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH5-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 9 | Pulse | - | Operator | Select then confirm
AH5-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH5, Auxiliary transformer feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 10 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH6-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 11 | Pulse | - | Operator | Select then confirm
AH6-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH6, Prime Minister feeder | 11 kV switchroom | DO | 1 | R1-CO01 | DO-8221 | 12 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH7-CB-OPEN-CMD | Open circuit breaker | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DO | 1 | R1-CO02 | DO-8221 | 1 | Pulse | - | Operator | Select then confirm
AH7-CB-CLOSE-CMD | Close circuit breaker | 11 kV panel AH7, Spare feeder | 11 kV switchroom | DO | 1 | R1-CO02 | DO-8221 | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed
AH8-NER-EF | Earth fault current alarm | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI04 | DI-8112 | 16 | Normally open | 1 | -
AH8-NER-TEMP | Resistor temperature high | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 1 | Normally open | 2 | -
AH8-AUX-OK | Panel supply healthy | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 2 | Normally closed | 2 | -
AH8-CB-OPEN | Circuit breaker open | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 3 | Status | Status | - | Added rev 1. The 11 kV system is earthed only through AH8
AH8-CB-CLSD | Circuit breaker closed | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 4 | Status | Status | - | Added rev 1. Level 1 alarm if open while the busbar is live
AH8-CB-TRIP | Circuit breaker tripped by protection | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 5 | Normally open | 1 | - | Added rev 1
AH8-ES-CLSD | Earth switch closed | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 6 | Status | Status | - | Added rev 1
AH8-GAS-LOW | Gas pressure low | 11 kV panel AH8, neutral earthing resistor | 11 kV switchroom | DI | 1 | R1-DI05 | DI-8112 | 7 | Normally open | 2 | - | Added rev 1
SYS-BEACON | Critical alarm beacon and sounder | Control room alarm beacon | Control room | DO | 1 | R1-DO01 | DO-8212 | 1 | De-energised | - | Automatic
SYS-CP-HEALTHY | Controller healthy output (watchdog) | SICAM CP-8050 | 11 kV switchroom | DO | 1 | R1-DO01 | DO-8212 | 2 | Energised | - | Automatic
T-AUX-OT-ALM | Oil temperature alarm | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 1 | Normally open | 3 | -
T-AUX-OT-TRIP | Oil temperature trip | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 2 | Normally open | 1 | -
T-AUX-WT-ALM | Winding temperature alarm | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 3 | Normally open | 3 | -
T-AUX-WT-TRIP | Winding temperature trip | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 4 | Normally open | 1 | -
T-AUX-PRD | Pressure relief device operated | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 5 | Normally open | 1 | -
T-AUX-OL-LOW | Oil level low | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 6 | Normally open | 2 | -
T-AUX-FUSE | HV fuse blown (XRNT-3A striker) | Auxiliary transformer 100 kVA | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 7 | Normally open | 1 | - | Added rev 1. The fuse is the only HV protection of this transformer
T-INV-OT-ALM | Oil temperature alarm | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 1 | Normally open | 3 | -
T-INV-OT-TRIP | Oil temperature trip | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 2 | Normally open | 1 | -
T-INV-WT-ALM | Winding temperature alarm | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 3 | Normally open | 3 | -
T-INV-WT-TRIP | Winding temperature trip | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 4 | Normally open | 1 | -
T-INV-PRD | Pressure relief device operated | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 5 | Normally open | 1 | -
T-INV-OL-LOW | Oil level low | Inverter transformer | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 6 | Normally open | 2 | -
PV-ACB-CLSD | PV main LV breaker (ACB 1250 A) closed | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 3 | Status | Status | - | Added rev 1
PV-ACB-TRIP | PV main LV breaker (ACB 1250 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 4 | Normally open | 1 | - | Added rev 1
NB01-MCCB-TRIP | Inverter NB01 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 5 | Normally open | 2 | - | Added rev 1
NB02-MCCB-TRIP | Inverter NB02 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 6 | Normally open | 2 | - | Added rev 1
NB03-MCCB-TRIP | Inverter NB03 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 7 | Normally open | 2 | - | Added rev 1
NB04-MCCB-TRIP | Inverter NB04 AC breaker (MCCB 400 A) tripped | PV LV switchboard 0.8 kV (AC combiner) | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 8 | Normally open | 2 | - | Added rev 1
BESS-ACB-CLSD | Battery main LV breaker (ACB 1000 A) closed | BESS LV breaker 0.69 kV | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 9 | Status | Status | - | Added rev 1
BESS-ACB-TRIP | Battery main LV breaker (ACB 1000 A) tripped | BESS LV breaker 0.69 kV | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 10 | Normally open | 1 | - | Added rev 1
T-DG-OT-ALM | Oil temperature alarm | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 1 | Normally open | 3 | -
T-DG-OT-TRIP | Oil temperature trip | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 2 | Normally open | 1 | -
T-DG-WT-ALM | Winding temperature alarm | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 3 | Normally open | 3 | -
T-DG-WT-TRIP | Winding temperature trip | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 4 | Normally open | 1 | -
T-DG-PRD | Pressure relief device operated | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 5 | Normally open | 1 | -
T-DG-OL-LOW | Oil level low | Generator step-up transformer | Generator area | DI | 6 | R6-DI01 | DI-8112 | 6 | Normally open | 2 | -
GEN-ACB-CLSD | DG step-up transformer LV breaker closed | Generator step-up transformer | Generator area | DI | 6 | R6-DI02 | DI-8112 | 1 | Status | Status | - | Added rev 1
GEN-ACB-TRIP | DG step-up transformer LV breaker tripped | Generator step-up transformer | Generator area | DI | 6 | R6-DI02 | DI-8112 | 2 | Normally open | 1 | - | Added rev 1
DG1-GCB-CLSD | Generator breaker closed | Diesel generator DG1 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 7 | Status | Status | - | Backup to Modbus status
DG1-COM-ALM | Common alarm | Diesel generator DG1 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 8 | Normally open | 2 | -
DG1-ESTOP | Emergency stop active | Diesel generator DG1 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 9 | Normally open | 1 | -
DG1-RUN | Engine running | Diesel generator DG1 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 10 | Status | Status | -
DG2-GCB-CLSD | Generator breaker closed | Diesel generator DG2 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 11 | Status | Status | - | Backup to Modbus status
DG2-COM-ALM | Common alarm | Diesel generator DG2 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 12 | Normally open | 2 | -
DG2-ESTOP | Emergency stop active | Diesel generator DG2 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 13 | Normally open | 1 | -
DG2-RUN | Engine running | Diesel generator DG2 | Generator area | DI | 6 | R6-DI01 | DI-8112 | 14 | Status | Status | -
FIRE-PREALM | Pre-alarm | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 7 | Normally open | 2 | - | Reset at panel only
FIRE-ALM | Fire alarm | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 8 | Normally open | 1 | - | Reset at panel only
FIRE-FLT | System fault | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 9 | Normally open | 2 | - | Reset at panel only
FIRE-REL | Suppression released | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 10 | Normally open | 1 | - | Reset at panel only
FIRE-AGENT-LOW | Agent pressure low | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 11 | Normally open | 2 | - | Reset at panel only
FIRE-ISOL | System isolated | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 12 | Normally open | 2 | - | Reset at panel only
FIRE-MAN-REL | Manual release activated | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 13 | Normally open | 1 | - | Reset at panel only
FIRE-PSU-FLT | Panel supply fault | Fire detection and suppression panel | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 14 | Normally open | 2 | - | Reset at panel only
AUXLV-INC-CLSD | Auxiliary LV incomer closed | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 7 | Status | Status | -
AUXLV-INC-TRIP | Auxiliary LV incomer tripped | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 8 | Normally open | 2 | -
AUXLV-SPD-FLT | Surge arrester failed | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 9 | Normally open | 3 | -
UPS-ON-BATT | UPS on battery | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 10 | Normally open | 2 | -
UPS-BATT-LOW | UPS battery low | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 11 | Normally open | 1 | -
UPS-FLT | UPS fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 12 | Normally open | 2 | -
UPS-BYPASS | UPS on bypass | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 13 | Normally open | 3 | -
DC-CHG-FLT | DC charger fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 14 | Normally open | 2 | -
DC-EARTH-FLT | DC earth fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 15 | Normally open | 2 | -
DC-UV | DC bus undervoltage | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI01 | DI-8112 | 16 | Normally open | 1 | -
SWR-HVAC-FLT | Switchroom air conditioning fault | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 1 | Normally open | 3 | -
SWR-TEMP-HI | Switchroom temperature high | Auxiliary supplies and UPS | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 2 | Normally open | 3 | -
ESTOP-SWR | Plant emergency stop pressed, switchroom | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 3 | Normally open | 1 | -
DOOR-SCADA | SCADA cabinet door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 4 | Normally open | 3 | -
DOOR-SWR | Switchroom door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 5 | Normally open | 3 | -
DOOR-GIS | 11 kV switchgear room door open | Emergency stops, doors and I/O panels | 11 kV switchroom | DI | 2 | R2-DI02 | DI-8112 | 6 | Normally open | 3 | -
ESTOP-BESS | Plant emergency stop pressed, BESS area | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 15 | Normally open | 1 | -
DOOR-BESS | BESS container door open | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | 5 | R5-DI01 | DI-8112 | 16 | Normally open | 3 | -
YARD-PNL-SUP-OK | Yard I/O panel supply healthy | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 1 | Normally closed | 2 | -
YARD-PNL-DOOR | Yard I/O panel door open | Emergency stops, doors and I/O panels | BESS and inverter transformer yard | DI | 5 | R5-DI02 | DI-8112 | 2 | Normally open | 3 | -
GEN-PNL-SUP-OK | Generator I/O panel supply healthy | Emergency stops, doors and I/O panels | Generator area | DI | 6 | R6-DI01 | DI-8112 | 15 | Normally closed | 2 | -
GEN-PNL-DOOR | Generator I/O panel door open | Emergency stops, doors and I/O panels | Generator area | DI | 6 | R6-DI01 | DI-8112 | 16 | Normally open | 3 | -
DG1-FUEL | Fuel tank level | Diesel generator DG1 | Generator area | AI | 6 | R6-AI01 | AI-8320 | 1 | 4-20 mA = 0-100 % | 3 below 20 % | -
DG2-FUEL | Fuel tank level | Diesel generator DG2 | Generator area | AI | 6 | R6-AI01 | AI-8320 | 2 | 4-20 mA = 0-100 % | 3 below 20 % | -
DC-110-V | 110 V DC bus voltage | Auxiliary supplies and UPS | 11 kV switchroom | AI | 2 | R2-AI01 | AI-8320 | 1 | 4-20 mA = 0-150 V | 2 outside limits | -
DC-24-V | 24 V DC bus voltage | Auxiliary supplies and UPS | 11 kV switchroom | AI | 2 | R2-AI01 | AI-8320 | 2 | 4-20 mA = 0-36 V | 2 outside limits | -
PRS-RS1-OPEN | Ring switch 1 open | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 1 | Status | Status | -
PRS-RS1-CLSD | Ring switch 1 closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 2 | Status | Status | -
PRS-RS1-ES | Ring switch 1 earth switch closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 3 | Status | Status | -
PRS-RS2-OPEN | Ring switch 2 open | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 4 | Status | Status | -
PRS-RS2-CLSD | Ring switch 2 closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 5 | Status | Status | -
PRS-RS2-ES | Ring switch 2 earth switch closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 6 | Status | Status | -
PRS-CB-OPEN | Transformer breaker open | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 7 | Status | Status | -
PRS-CB-CLSD | Transformer breaker closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 8 | Status | Status | -
PRS-CB-ES | Transformer breaker earth switch closed | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 9 | Status | Status | -
PRS-CB-TRIP | Transformer breaker tripped by ST260E | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 10 | Normally open | 1 | -
PRS-GAS-LOW | RMU gas pressure low | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 11 | Normally open | 2 | -
PRS-LR-REM | RMU local/remote in remote | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 12 | Status | Status | -
PRS-FPI | Fault passage indicator operated | President station RMU | President station | DI | 3 | R3-DI01 | DI-8112 | 13 | Normally open | 2 | -
PRS-TX-OT-ALM | Oil temperature alarm | President station transformer 630 kVA | President station | DI | 3 | R3-DI01 | DI-8112 | 14 | Normally open | 3 | -
PRS-TX-OT-TRIP | Oil temperature trip | President station transformer 630 kVA | President station | DI | 3 | R3-DI01 | DI-8112 | 15 | Normally open | 1 | -
PRS-TX-WT-ALM | Winding temperature alarm | President station transformer 630 kVA | President station | DI | 3 | R3-DI01 | DI-8112 | 16 | Normally open | 3 | -
PRS-TX-WT-TRIP | Winding temperature trip | President station transformer 630 kVA | President station | DI | 3 | R3-DI02 | DI-8112 | 1 | Normally open | 1 | -
PRS-TX-PRD | Pressure relief device operated | President station transformer 630 kVA | President station | DI | 3 | R3-DI02 | DI-8112 | 2 | Normally open | 1 | -
PRS-TX-OL-LOW | Oil level low | President station transformer 630 kVA | President station | DI | 3 | R3-DI02 | DI-8112 | 3 | Normally open | 2 | -
PRS-LV-INC-CLSD | LV incomer closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 4 | Status | Status | -
PRS-LV-INC-TRIP | LV incomer tripped | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 5 | Normally open | 2 | -
PRS-LV-F01-CLSD | Outgoing way 1 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 6 | Status | Status | -
PRS-LV-F02-CLSD | Outgoing way 2 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 7 | Status | Status | -
PRS-LV-F03-CLSD | Outgoing way 3 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 8 | Status | Status | -
PRS-LV-F04-CLSD | Outgoing way 4 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 9 | Status | Status | -
PRS-LV-F05-CLSD | Outgoing way 5 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 10 | Status | Status | -
PRS-LV-F06-CLSD | Outgoing way 6 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 11 | Status | Status | -
PRS-LV-F07-CLSD | Outgoing way 7 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 12 | Status | Status | -
PRS-LV-F08-CLSD | Outgoing way 8 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 13 | Status | Status | -
PRS-LV-F09-CLSD | Outgoing way 9 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 14 | Status | Status | -
PRS-LV-F10-CLSD | Outgoing way 10 closed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 15 | Status | Status | -
PRS-LV-SPD-FLT | Surge arrester failed | President station LVDB | President station | DI | 3 | R3-DI02 | DI-8112 | 16 | Normally open | 3 | -
PRS-PNL-SUP-OK | I/O panel supply healthy | President station LVDB | President station | DI | 3 | R3-DI03 | DI-8112 | 1 | Normally closed | 2 | -
PRS-UPS-ON-BATT | RMU UPS 2 kVA on battery | President station RMU | President station | DI | 3 | R3-DI03 | DI-8112 | 2 | Normally open | 2 | - | Added rev 1. UPS shown on the transformer stations drawing
PRS-UPS-FLT | RMU UPS 2 kVA fault | President station RMU | President station | DI | 3 | R3-DI03 | DI-8112 | 3 | Normally open | 2 | - | Added rev 1
PRS-RS1-OPEN-CMD | Open ring switch 1 | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 1 | Pulse | - | Operator | Select then confirm
PRS-RS1-CLOSE-CMD | Close ring switch 1 | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed
PRS-RS2-OPEN-CMD | Open ring switch 2 | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 3 | Pulse | - | Operator | Select then confirm
PRS-RS2-CLOSE-CMD | Close ring switch 2 | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed
PRS-CB-OPEN-CMD | Open transformer breaker | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 5 | Pulse | - | Operator | Select then confirm
PRS-CB-CLOSE-CMD | Close transformer breaker | President station RMU | President station | DO | 3 | R3-CO01 | DO-8221 | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed
PRS-LV-INC-OPEN-CMD | Open LV incomer | President station LVDB | President station | DO | 3 | R3-CO01 | DO-8221 | 7 | Pulse | - | Operator | Select then confirm
PRS-LV-INC-CLOSE-CMD | Close LV incomer | President station LVDB | President station | DO | 3 | R3-CO01 | DO-8221 | 8 | Pulse | - | Operator | Select then confirm
PMS-RS1-OPEN | Ring switch 1 open | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 1 | Status | Status | -
PMS-RS1-CLSD | Ring switch 1 closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 2 | Status | Status | -
PMS-RS1-ES | Ring switch 1 earth switch closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 3 | Status | Status | -
PMS-RS2-OPEN | Ring switch 2 open | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 4 | Status | Status | -
PMS-RS2-CLSD | Ring switch 2 closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 5 | Status | Status | -
PMS-RS2-ES | Ring switch 2 earth switch closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 6 | Status | Status | -
PMS-CB-OPEN | Transformer breaker open | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 7 | Status | Status | -
PMS-CB-CLSD | Transformer breaker closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 8 | Status | Status | -
PMS-CB-ES | Transformer breaker earth switch closed | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 9 | Status | Status | -
PMS-CB-TRIP | Transformer breaker tripped by ST260E | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 10 | Normally open | 1 | -
PMS-GAS-LOW | RMU gas pressure low | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 11 | Normally open | 2 | -
PMS-LR-REM | RMU local/remote in remote | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 12 | Status | Status | -
PMS-FPI | Fault passage indicator operated | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 13 | Normally open | 2 | -
PMS-TX-OT-ALM | Oil temperature alarm | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 14 | Normally open | 3 | -
PMS-TX-OT-TRIP | Oil temperature trip | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 15 | Normally open | 1 | -
PMS-TX-WT-ALM | Winding temperature alarm | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI01 | DI-8112 | 16 | Normally open | 3 | -
PMS-TX-WT-TRIP | Winding temperature trip | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 1 | Normally open | 1 | -
PMS-TX-PRD | Pressure relief device operated | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 2 | Normally open | 1 | -
PMS-TX-OL-LOW | Oil level low | Prime Minister station transformer 630 kVA | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 3 | Normally open | 2 | -
PMS-LV-INC-CLSD | LV incomer closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 4 | Status | Status | -
PMS-LV-INC-TRIP | LV incomer tripped | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 5 | Normally open | 2 | -
PMS-LV-F01-CLSD | Outgoing way 1 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 6 | Status | Status | -
PMS-LV-F02-CLSD | Outgoing way 2 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 7 | Status | Status | -
PMS-LV-F03-CLSD | Outgoing way 3 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 8 | Status | Status | -
PMS-LV-F04-CLSD | Outgoing way 4 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 9 | Status | Status | -
PMS-LV-F05-CLSD | Outgoing way 5 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 10 | Status | Status | -
PMS-LV-F06-CLSD | Outgoing way 6 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 11 | Status | Status | -
PMS-LV-F07-CLSD | Outgoing way 7 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 12 | Status | Status | -
PMS-LV-F08-CLSD | Outgoing way 8 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 13 | Status | Status | -
PMS-LV-F09-CLSD | Outgoing way 9 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 14 | Status | Status | -
PMS-LV-F10-CLSD | Outgoing way 10 closed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 15 | Status | Status | -
PMS-LV-SPD-FLT | Surge arrester failed | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI02 | DI-8112 | 16 | Normally open | 3 | -
PMS-PNL-SUP-OK | I/O panel supply healthy | Prime Minister station LVDB | Prime Minister station | DI | 4 | R4-DI03 | DI-8112 | 1 | Normally closed | 2 | -
PMS-UPS-ON-BATT | RMU UPS 2 kVA on battery | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI03 | DI-8112 | 2 | Normally open | 2 | - | Added rev 1. UPS shown on the transformer stations drawing
PMS-UPS-FLT | RMU UPS 2 kVA fault | Prime Minister station RMU | Prime Minister station | DI | 4 | R4-DI03 | DI-8112 | 3 | Normally open | 2 | - | Added rev 1
PMS-RS1-OPEN-CMD | Open ring switch 1 | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 1 | Pulse | - | Operator | Select then confirm
PMS-RS1-CLOSE-CMD | Close ring switch 1 | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 2 | Pulse | - | Operator | Select then confirm; blocked if earthed
PMS-RS2-OPEN-CMD | Open ring switch 2 | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 3 | Pulse | - | Operator | Select then confirm
PMS-RS2-CLOSE-CMD | Close ring switch 2 | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 4 | Pulse | - | Operator | Select then confirm; blocked if earthed
PMS-CB-OPEN-CMD | Open transformer breaker | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 5 | Pulse | - | Operator | Select then confirm
PMS-CB-CLOSE-CMD | Close transformer breaker | Prime Minister station RMU | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 6 | Pulse | - | Operator | Select then confirm; blocked if earthed
PMS-LV-INC-OPEN-CMD | Open LV incomer | Prime Minister station LVDB | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 7 | Pulse | - | Operator | Select then confirm
PMS-LV-INC-CLOSE-CMD | Close LV incomer | Prime Minister station LVDB | Prime Minister station | DO | 4 | R4-CO01 | DO-8221 | 8 | Pulse | - | Operator | Select then confirm

## IO Summary
I/O row | Location | Module | Module type | Channels | Used | Spare | Spare %
1 | 11 kV switchroom (local) | R1-DI01 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-DI02 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-DI03 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-DI04 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-DI05 | DI-8112 | 16
1 | 11 kV switchroom (local) | R1-CO01 | DO-8221 | 12
1 | 11 kV switchroom (local) | R1-CO02 | DO-8221 | 12
1 | 11 kV switchroom (local) | R1-DO01 | DO-8212 | 8
2 | 11 kV switchroom (CI-8532) | R2-DI01 | DI-8112 | 16
2 | 11 kV switchroom (CI-8532) | R2-DI02 | DI-8112 | 16
2 | 11 kV switchroom (CI-8532) | R2-AI01 | AI-8320 | 4
3 | President station (CI-8533) | R3-DI01 | DI-8112 | 16
3 | President station (CI-8533) | R3-DI02 | DI-8112 | 16
3 | President station (CI-8533) | R3-DI03 | DI-8112 | 16
3 | President station (CI-8533) | R3-CO01 | DO-8221 | 12
4 | Prime Minister station (CI-8533) | R4-DI01 | DI-8112 | 16
4 | Prime Minister station (CI-8533) | R4-DI02 | DI-8112 | 16
4 | Prime Minister station (CI-8533) | R4-DI03 | DI-8112 | 16
4 | Prime Minister station (CI-8533) | R4-CO01 | DO-8221 | 12
5 | BESS and inverter transformer yard (CI-8533) | R5-DI01 | DI-8112 | 16
5 | BESS and inverter transformer yard (CI-8533) | R5-DI02 | DI-8112 | 16
6 | Generator area (CI-8533) | R6-DI01 | DI-8112 | 16
6 | Generator area (CI-8533) | R6-DI02 | DI-8112 | 16
6 | Generator area (CI-8533) | R6-AI01 | AI-8320 | 4
Totals by module type
Module type | Description | Modules | Channels | Used | Spare | Spare %
DI-8112 | Digital input, 16
DO-8221 | Secured command output, 12
DO-8212 | Relay output, 8
AI-8320 | Analogue input, 4
Total
Hardwired signals by type
Type | Meaning | Signals
DI | Digital input (status, alarm)
DO | Digital output (command)
AI | Analogue input (4-20 mA)
Total

## IO Rows
I/O row | Location | Remote interface | Product number | Link to CP-8050 | Equipment wired to this row | I/O modules | Hardwired signals | Spare channels
1 | 11 kV switchroom, beside the CP-8050 | None (local row) | - | Backplane, no cable | 11 kV panels AH1 to AH8, alarm beacon, controller watchdog
2 | 11 kV switchroom, SCADA cabinet | CI-8532 (electrical) | 6MF2853-2AA00 | Copper, inside the cabinet | Auxiliary transformer, auxiliary LV board, UPS, DC supplies, switchroom E-stop and doors
3 | President office transformer station | CI-8533 (optical) | To confirm | Fibre pair, laid with the 11 kV cable | RMU, 630 kVA transformer, LVDB
4 | Prime Minister office transformer station | CI-8533 (optical) | To confirm | Fibre pair, laid with the 11 kV cable | RMU, 630 kVA transformer, LVDB
5 | BESS and inverter transformer yard | CI-8533 (optical) | To confirm | Spare fibre pair in the field switch 2 cable | Inverter transformer, battery fire panel, BESS E-stop and door, panel supervision
6 | Generator area | CI-8533 (optical) | To confirm | Spare fibre pair in the field switch 3 cable | DG1 and DG2 status and fuel level, DG step-up transformer, panel supervision
Total
Each remote row is a small panel near its equipment. Field contacts are wired a short distance to that panel; one link carries all signals to the CP-8050.
Rows within about 100 m of the switchroom may use CI-8532 on copper instead of CI-8533 on fibre. Fibre is preferred between buildings for surge and earth-potential immunity.
Confirm with Siemens: fibre type and maximum length for CI-8533, and whether the remote link can share a fibre cable with the plant network on separate cores.
The CP-8050 accepts up to 16 I/O rows of 8 modules, so the design uses 6 of 16 rows.

## Comms Points
Device | Source / protocol | Point | Direction | Data type | Unit | Devices | Points each | Total points | Operated by | Notes
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Active power | Read | Measured | kW | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Reactive power | Read | Measured | kvar | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | 4 | 3 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | AC current L1, L2, L3 (3 points) | Read | Measured | A | 4 | 3 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Frequency | Read | Measured | Hz | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Power factor | Read | Measured | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC voltage | Read | Measured | V | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC current | Read | Measured | A | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | DC power | Read | Measured | kW | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Energy today | Read | Counter | kWh | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Energy total | Read | Counter | MWh | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Internal temperature | Read | Measured | deg C | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Insulation resistance | Read | Measured | kohm | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Operating state | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Fault code | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Alarm code | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Communication healthy | Read | Status | - | 4 | 1 |  | -
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Active power limit | Write | Setpoint | % | 4 | 1 |  | Admin | Normally set by the EMS; write only if the EMS allows
PV inverter NB01 to NB04 | PLC box, Modbus TCP | Start / stop | Write | Command | - | 4 | 1 |  | Admin
Embedded EMS | Modbus TCP | Plant active power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Plant reactive power | Read | Measured | kvar | 1 | 1 |  | -
Embedded EMS | Modbus TCP | PV total power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | BESS power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Generator total power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Load power | Read | Measured | kW | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Bus voltage | Read | Measured | kV | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Bus frequency | Read | Measured | Hz | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Operating mode | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS state | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS summary alarm | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | Generator start request | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | PV curtailment active | Read | Status | - | 1 | 1 |  | -
Embedded EMS | Modbus TCP | EMS heartbeat | Read/Write | Counter | - | 1 | 1 |  | Automatic | Link supervision
Embedded EMS | Modbus TCP | Operating mode select | Write | Command | - | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | State of charge minimum | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | State of charge maximum | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | Generator start threshold | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | Generator stop threshold | Write | Setpoint | % | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | BESS power limit | Write | Setpoint | kW | 1 | 1 |  | Admin
Embedded EMS | Modbus TCP | BESS C-rate limit enable / disable | Write | Command | - | 1 | 1 |  | Admin | Calibration only; available only if the EMS exposes it
Embedded EMS | Modbus TCP | Fault reset, level 3 | Write | Command | - | 1 | 1 |  | Operator
Embedded EMS | Modbus TCP | Fault reset, levels 1 and 2 | Write | Command | - | 1 | 1 |  | Admin
Battery system ST3340UX | Through the EMS, Modbus TCP | State of charge | Read | Measured | % | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | State of health | Read | Measured | % | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC voltage | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC current | Read | Measured | A | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Active power | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Reactive power | Read | Measured | kvar | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell voltage maximum | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell voltage minimum | Read | Measured | V | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell temperature maximum | Read | Measured | deg C | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cell temperature minimum | Read | Measured | deg C | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Charge power limit | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Discharge power limit | Read | Measured | kW | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Energy charged total | Read | Counter | MWh | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Energy discharged total | Read | Counter | MWh | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Converter state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery management state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Racks online | Read | Measured | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | DC contactors closed | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Cooling system state | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 1 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 2 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Alarm level 3 | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Container fire status | Read | Status | - | 1 | 1 |  | -
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery combiner panel DC switch closed (2 points) | Read | Status | - | 1 | 2 |  | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
Battery system ST3340UX | Through the EMS, Modbus TCP | Battery combiner panel fuse blown (2 points) | Read | Status | - | 1 | 2 |  | - | Added rev 1. As above
Generator controller DG1, DG2 | Modbus TCP or RTU | Voltage L1, L2, L3 (3 points) | Read | Measured | V | 2 | 3 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Current L1, L2, L3 (3 points) | Read | Measured | A | 2 | 3 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Active power | Read | Measured | kW | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Reactive power | Read | Measured | kvar | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Power factor | Read | Measured | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Frequency | Read | Measured | Hz | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Oil pressure | Read | Measured | kPa | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Coolant temperature | Read | Measured | deg C | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Starter battery voltage | Read | Measured | V | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Fuel level | Read | Measured | % | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Running hours | Read | Counter | h | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Number of starts | Read | Counter | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Energy total | Read | Counter | MWh | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Controller mode | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Breaker status | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Warning | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Shutdown alarm | Read | Status | - | 2 | 1 |  | -
Generator controller DG1, DG2 | Modbus TCP or RTU | Start | Write | Command | - | 2 | 1 |  | Operator | Only in manual mode
Generator controller DG1, DG2 | Modbus TCP or RTU | Stop | Write | Command | - | 2 | 1 |  | Operator | Only in manual mode
Generator controller DG1, DG2 | Modbus TCP or RTU | Mode auto / manual | Write | Command | - | 2 | 1 |  | Admin
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Phase current L1, L2, L3 (3 points) | Read | Measured | A | 7 | 3 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Earth current | Read | Measured | A | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | 7 | 3 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Active power | Read | Measured | kW | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Reactive power | Read | Measured | kvar | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Power factor | Read | Measured | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Frequency | Read | Measured | Hz | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Energy import | Read | Counter | MWh | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Energy export | Read | Counter | MWh | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Breaker position | Read | Double point | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Overcurrent trip (50/51) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Earth fault trip (50N/51N) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Under / overvoltage trip (27/59) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Frequency trip (81) | Read | Event | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Relay healthy | Read | Status | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Disturbance record available | Read | Status | - | 7 | 1 |  | -
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Trip circuit supervision alarm | Read | Status | - | 7 | 1 |  | - | Added rev 1
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Sensitive earth fault trip (51G) | Read | Event | - | 6 | 1 |  | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
11 kV protection relay AH1 to AH7 | IEC 61850 or Modbus TCP | Reverse power trip (32), AH1 generator incomer | Read | Event | - | 1 | 1 |  | - | Added rev 1. Protects the generators against reverse power from PV and battery
RMU relay ST260E | Modbus RTU through MGate | Phase current L1, L2, L3 (3 points) | Read | Measured | A | 2 | 3 |  | -
RMU relay ST260E | Modbus RTU through MGate | Earth current | Read | Measured | A | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through MGate | Breaker position | Read | Double point | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through MGate | Overcurrent trip | Read | Event | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through MGate | Earth fault trip | Read | Event | - | 2 | 1 |  | -
RMU relay ST260E | Modbus RTU through MGate | Relay healthy | Read | Status | - | 2 | 1 |  | -
Power meter PM5560 | Modbus TCP | Voltage L-N, 3 phases (3 points) | Read | Measured | V | 3 | 3 |  | -
Power meter PM5560 | Modbus TCP | Current, 3 phases (3 points) | Read | Measured | A | 3 | 3 |  | -
Power meter PM5560 | Modbus TCP | Active power | Read | Measured | kW | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Reactive power | Read | Measured | kvar | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Apparent power | Read | Measured | kVA | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Power factor | Read | Measured | - | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Frequency | Read | Measured | Hz | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Active energy | Read | Counter | kWh | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Reactive energy | Read | Counter | kvarh | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Voltage THD | Read | Measured | % | 3 | 1 |  | -
Power meter PM5560 | Modbus TCP | Current THD | Read | Measured | % | 3 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Plane-of-array irradiance | Read | Measured | W/m2 | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Wind speed | Read | Measured | m/s | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Wind direction | Read | Measured | deg | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Ambient temperature | Read | Measured | deg C | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Module temperature | Read | Measured | deg C | 1 | 1 |  | -
Weather logger blue'Log XM | Modbus TCP | Logger healthy | Read | Status | - | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Input voltage | Read | Measured | V | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Output load | Read | Measured | % | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Battery charge | Read | Measured | % | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Runtime remaining | Read | Measured | min | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | On battery | Read | Status | - | 1 | 1 |  | -
UPS | Modbus TCP or SNMP | Fault | Read | Status | - | 1 | 1 |  | -
Network switches (core and field) | SNMP v3 | Device healthy | Read | Status | - | 7 | 1 |  | -
Network switches (core and field) | SNMP v3 | Ring status | Read | Status | - | 7 | 1 |  | -
Firewall and GPS time server | SNMP v3 | Device healthy | Read | Status | - | 2 | 1 |  | -
Firewall and GPS time server | SNMP v3 | Time synchronised / VPN session active | Read | Status | - | 2 | 1 |  | -
PLC box | Modbus TCP | Communication healthy per inverter (4 points) | Read | Status | - | 1 | 4 |  | -
SICAM CP-8050 internal | Internal | Controller healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | Power supply 1 healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | Power supply 2 healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 1 healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 2 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 3 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 4 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 5 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | I/O row 6 link healthy | Read | Status | - | 1 | 1 |  | -
SICAM CP-8050 internal | Internal | Link to each communication device healthy (8 links) | Read | Status | - | 1 | 8 |  | -
Total
Read
Write
Typical points only. Replace each block with the vendor's point table when received.

## Comms Point List
Tag | Device | Point | Direction | Data type | Unit | Source / protocol | Alarm level | Alarm when | Operated by | Notes
NB01-P | PV inverter NB01 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB01-Q | PV inverter NB01 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB01-U-L1 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-U-L2 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-U-L3 | PV inverter NB01 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-I-L1 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-I-L2 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-I-L3 | PV inverter NB01 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-F | PV inverter NB01 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB01-PF | PV inverter NB01 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB01-U-DC | PV inverter NB01 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB01-I-DC | PV inverter NB01 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB01-P-DC | PV inverter NB01 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB01-E-DAY | PV inverter NB01 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB01-E-TOT | PV inverter NB01 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB01-T-INT | PV inverter NB01 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB01-R-ISO | PV inverter NB01 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB01-STATE | PV inverter NB01 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-FLT-CODE | PV inverter NB01 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-ALM-CODE | PV inverter NB01 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB01-COMM-OK | PV inverter NB01 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB01-P-LIM-SP | PV inverter NB01 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB01-START-STOP-CMD | PV inverter NB01 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB02-P | PV inverter NB02 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB02-Q | PV inverter NB02 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB02-U-L1 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-U-L2 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-U-L3 | PV inverter NB02 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-I-L1 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-I-L2 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-I-L3 | PV inverter NB02 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-F | PV inverter NB02 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB02-PF | PV inverter NB02 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB02-U-DC | PV inverter NB02 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB02-I-DC | PV inverter NB02 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB02-P-DC | PV inverter NB02 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB02-E-DAY | PV inverter NB02 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB02-E-TOT | PV inverter NB02 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB02-T-INT | PV inverter NB02 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB02-R-ISO | PV inverter NB02 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB02-STATE | PV inverter NB02 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-FLT-CODE | PV inverter NB02 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-ALM-CODE | PV inverter NB02 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB02-COMM-OK | PV inverter NB02 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB02-P-LIM-SP | PV inverter NB02 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB02-START-STOP-CMD | PV inverter NB02 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB03-P | PV inverter NB03 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB03-Q | PV inverter NB03 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB03-U-L1 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-U-L2 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-U-L3 | PV inverter NB03 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-I-L1 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-I-L2 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-I-L3 | PV inverter NB03 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-F | PV inverter NB03 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB03-PF | PV inverter NB03 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB03-U-DC | PV inverter NB03 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB03-I-DC | PV inverter NB03 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB03-P-DC | PV inverter NB03 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB03-E-DAY | PV inverter NB03 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB03-E-TOT | PV inverter NB03 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB03-T-INT | PV inverter NB03 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB03-R-ISO | PV inverter NB03 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB03-STATE | PV inverter NB03 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-FLT-CODE | PV inverter NB03 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-ALM-CODE | PV inverter NB03 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB03-COMM-OK | PV inverter NB03 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB03-P-LIM-SP | PV inverter NB03 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB03-START-STOP-CMD | PV inverter NB03 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
NB04-P | PV inverter NB04 | Active power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB04-Q | PV inverter NB04 | Reactive power | Read | Measured | kvar | PLC box, Modbus TCP | - | - | -
NB04-U-L1 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-U-L2 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-U-L3 | PV inverter NB04 | AC voltage L1, L2, L3 (3 points) | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-I-L1 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-I-L2 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-I-L3 | PV inverter NB04 | AC current L1, L2, L3 (3 points) | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-F | PV inverter NB04 | Frequency | Read | Measured | Hz | PLC box, Modbus TCP | - | - | -
NB04-PF | PV inverter NB04 | Power factor | Read | Measured | - | PLC box, Modbus TCP | - | - | -
NB04-U-DC | PV inverter NB04 | DC voltage | Read | Measured | V | PLC box, Modbus TCP | - | - | -
NB04-I-DC | PV inverter NB04 | DC current | Read | Measured | A | PLC box, Modbus TCP | - | - | -
NB04-P-DC | PV inverter NB04 | DC power | Read | Measured | kW | PLC box, Modbus TCP | - | - | -
NB04-E-DAY | PV inverter NB04 | Energy today | Read | Counter | kWh | PLC box, Modbus TCP | - | - | -
NB04-E-TOT | PV inverter NB04 | Energy total | Read | Counter | MWh | PLC box, Modbus TCP | - | - | -
NB04-T-INT | PV inverter NB04 | Internal temperature | Read | Measured | deg C | PLC box, Modbus TCP | - | - | -
NB04-R-ISO | PV inverter NB04 | Insulation resistance | Read | Measured | kohm | PLC box, Modbus TCP | - | - | -
NB04-STATE | PV inverter NB04 | Operating state | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-FLT-CODE | PV inverter NB04 | Fault code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-ALM-CODE | PV inverter NB04 | Alarm code | Read | Status | - | PLC box, Modbus TCP | Status | - | -
NB04-COMM-OK | PV inverter NB04 | Communication healthy | Read | Status | - | PLC box, Modbus TCP | 2 | Off | -
NB04-P-LIM-SP | PV inverter NB04 | Active power limit | Write | Setpoint | % | PLC box, Modbus TCP | - | - | Admin | Normally set by the EMS; write only if the EMS allows
NB04-START-STOP-CMD | PV inverter NB04 | Start / stop | Write | Command | - | PLC box, Modbus TCP | - | - | Admin
EMS-P-PLANT | Embedded EMS | Plant active power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-Q-PLANT | Embedded EMS | Plant reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
EMS-P-PV | Embedded EMS | PV total power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-BESS | Embedded EMS | BESS power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-GEN | Embedded EMS | Generator total power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-P-LOAD | Embedded EMS | Load power | Read | Measured | kW | Modbus TCP | - | - | -
EMS-U-BUS | Embedded EMS | Bus voltage | Read | Measured | kV | Modbus TCP | - | - | -
EMS-F-BUS | Embedded EMS | Bus frequency | Read | Measured | Hz | Modbus TCP | - | - | -
EMS-MODE | Embedded EMS | Operating mode | Read | Status | - | Modbus TCP | Status | - | -
EMS-STATE | Embedded EMS | EMS state | Read | Status | - | Modbus TCP | Status | - | -
EMS-ALM | Embedded EMS | EMS summary alarm | Read | Status | - | Modbus TCP | 2 | On | -
EMS-GEN-START-REQ | Embedded EMS | Generator start request | Read | Status | - | Modbus TCP | 3 | On | -
EMS-PV-CURT | Embedded EMS | PV curtailment active | Read | Status | - | Modbus TCP | 3 | On | -
EMS-HEARTBEAT | Embedded EMS | EMS heartbeat | Read/Write | Counter | - | Modbus TCP | - | - | Automatic | Link supervision
EMS-MODE-CMD | Embedded EMS | Operating mode select | Write | Command | - | Modbus TCP | - | - | Admin
EMS-SOC-MIN-SP | Embedded EMS | State of charge minimum | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-SOC-MAX-SP | Embedded EMS | State of charge maximum | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-GEN-START-SP | Embedded EMS | Generator start threshold | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-GEN-STOP-SP | Embedded EMS | Generator stop threshold | Write | Setpoint | % | Modbus TCP | - | - | Admin
EMS-P-BESS-LIM-SP | Embedded EMS | BESS power limit | Write | Setpoint | kW | Modbus TCP | - | - | Admin
EMS-CRATE-CMD | Embedded EMS | BESS C-rate limit enable / disable | Write | Command | - | Modbus TCP | - | - | Admin | Calibration only; available only if the EMS exposes it
EMS-RESET-L3-CMD | Embedded EMS | Fault reset, level 3 | Write | Command | - | Modbus TCP | - | - | Operator
EMS-RESET-L12-CMD | Embedded EMS | Fault reset, levels 1 and 2 | Write | Command | - | Modbus TCP | - | - | Admin
BESS-SOC | Battery system ST3340UX | State of charge | Read | Measured | % | Through the EMS, Modbus TCP | - | - | -
BESS-SOH | Battery system ST3340UX | State of health | Read | Measured | % | Through the EMS, Modbus TCP | - | - | -
BESS-U-DC | Battery system ST3340UX | DC voltage | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-I-DC | Battery system ST3340UX | DC current | Read | Measured | A | Through the EMS, Modbus TCP | - | - | -
BESS-P | Battery system ST3340UX | Active power | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-Q | Battery system ST3340UX | Reactive power | Read | Measured | kvar | Through the EMS, Modbus TCP | - | - | -
BESS-U-CELL-MAX | Battery system ST3340UX | Cell voltage maximum | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-U-CELL-MIN | Battery system ST3340UX | Cell voltage minimum | Read | Measured | V | Through the EMS, Modbus TCP | - | - | -
BESS-T-CELL-MAX | Battery system ST3340UX | Cell temperature maximum | Read | Measured | deg C | Through the EMS, Modbus TCP | - | - | -
BESS-T-CELL-MIN | Battery system ST3340UX | Cell temperature minimum | Read | Measured | deg C | Through the EMS, Modbus TCP | - | - | -
BESS-P-CHG-LIM | Battery system ST3340UX | Charge power limit | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-P-DIS-LIM | Battery system ST3340UX | Discharge power limit | Read | Measured | kW | Through the EMS, Modbus TCP | - | - | -
BESS-E-CHG | Battery system ST3340UX | Energy charged total | Read | Counter | MWh | Through the EMS, Modbus TCP | - | - | -
BESS-E-DIS | Battery system ST3340UX | Energy discharged total | Read | Counter | MWh | Through the EMS, Modbus TCP | - | - | -
BESS-PCS-STATE | Battery system ST3340UX | Converter state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-BMS-STATE | Battery system ST3340UX | Battery management state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-RACKS-ON | Battery system ST3340UX | Racks online | Read | Measured | - | Through the EMS, Modbus TCP | - | - | -
BESS-DC-CONT | Battery system ST3340UX | DC contactors closed | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-COOL-STATE | Battery system ST3340UX | Cooling system state | Read | Status | - | Through the EMS, Modbus TCP | Status | - | -
BESS-ALM-L1 | Battery system ST3340UX | Alarm level 1 | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | -
BESS-ALM-L2 | Battery system ST3340UX | Alarm level 2 | Read | Status | - | Through the EMS, Modbus TCP | 2 | On | -
BESS-ALM-L3 | Battery system ST3340UX | Alarm level 3 | Read | Status | - | Through the EMS, Modbus TCP | 3 | On | -
BESS-FIRE | Battery system ST3340UX | Container fire status | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | -
BESS-BCP1-SW-CLSD | Battery system ST3340UX | Battery combiner panel DC switch closed (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 2 | On | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
BESS-BCP2-SW-CLSD | Battery system ST3340UX | Battery combiner panel DC switch closed (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 2 | On | - | Added rev 1. Combiner panels BCP unit 1# and 2#, if the EMS exposes them
BESS-BCP1-FUSE | Battery system ST3340UX | Battery combiner panel fuse blown (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | - | Added rev 1. As above
BESS-BCP2-FUSE | Battery system ST3340UX | Battery combiner panel fuse blown (2 points) | Read | Status | - | Through the EMS, Modbus TCP | 1 | On | - | Added rev 1. As above
DG1-U-L1 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-U-L2 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-U-L3 | Generator controller DG1 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-I-L1 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-I-L2 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-I-L3 | Generator controller DG1 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG1-P | Generator controller DG1 | Active power | Read | Measured | kW | Modbus TCP or RTU | - | - | -
DG1-Q | Generator controller DG1 | Reactive power | Read | Measured | kvar | Modbus TCP or RTU | - | - | -
DG1-PF | Generator controller DG1 | Power factor | Read | Measured | - | Modbus TCP or RTU | - | - | -
DG1-F | Generator controller DG1 | Frequency | Read | Measured | Hz | Modbus TCP or RTU | - | - | -
DG1-OIL-P | Generator controller DG1 | Oil pressure | Read | Measured | kPa | Modbus TCP or RTU | - | - | -
DG1-COOL-T | Generator controller DG1 | Coolant temperature | Read | Measured | deg C | Modbus TCP or RTU | - | - | -
DG1-BATT-U | Generator controller DG1 | Starter battery voltage | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG1-FUEL-COM | Generator controller DG1 | Fuel level | Read | Measured | % | Modbus TCP or RTU | - | - | - | Communicated copy of hardwired signal DG1-FUEL
DG1-HOURS | Generator controller DG1 | Running hours | Read | Counter | h | Modbus TCP or RTU | - | - | -
DG1-STARTS | Generator controller DG1 | Number of starts | Read | Counter | - | Modbus TCP or RTU | - | - | -
DG1-E-TOT | Generator controller DG1 | Energy total | Read | Counter | MWh | Modbus TCP or RTU | - | - | -
DG1-MODE | Generator controller DG1 | Controller mode | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG1-GCB | Generator controller DG1 | Breaker status | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG1-WARN | Generator controller DG1 | Warning | Read | Status | - | Modbus TCP or RTU | 3 | On | -
DG1-SHUTDOWN | Generator controller DG1 | Shutdown alarm | Read | Status | - | Modbus TCP or RTU | 1 | On | -
DG1-START-CMD | Generator controller DG1 | Start | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG1-STOP-CMD | Generator controller DG1 | Stop | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG1-MODE-CMD | Generator controller DG1 | Mode auto / manual | Write | Command | - | Modbus TCP or RTU | - | - | Admin
DG2-U-L1 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-U-L2 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-U-L3 | Generator controller DG2 | Voltage L1, L2, L3 (3 points) | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-I-L1 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-I-L2 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-I-L3 | Generator controller DG2 | Current L1, L2, L3 (3 points) | Read | Measured | A | Modbus TCP or RTU | - | - | -
DG2-P | Generator controller DG2 | Active power | Read | Measured | kW | Modbus TCP or RTU | - | - | -
DG2-Q | Generator controller DG2 | Reactive power | Read | Measured | kvar | Modbus TCP or RTU | - | - | -
DG2-PF | Generator controller DG2 | Power factor | Read | Measured | - | Modbus TCP or RTU | - | - | -
DG2-F | Generator controller DG2 | Frequency | Read | Measured | Hz | Modbus TCP or RTU | - | - | -
DG2-OIL-P | Generator controller DG2 | Oil pressure | Read | Measured | kPa | Modbus TCP or RTU | - | - | -
DG2-COOL-T | Generator controller DG2 | Coolant temperature | Read | Measured | deg C | Modbus TCP or RTU | - | - | -
DG2-BATT-U | Generator controller DG2 | Starter battery voltage | Read | Measured | V | Modbus TCP or RTU | - | - | -
DG2-FUEL-COM | Generator controller DG2 | Fuel level | Read | Measured | % | Modbus TCP or RTU | - | - | - | Communicated copy of hardwired signal DG2-FUEL
DG2-HOURS | Generator controller DG2 | Running hours | Read | Counter | h | Modbus TCP or RTU | - | - | -
DG2-STARTS | Generator controller DG2 | Number of starts | Read | Counter | - | Modbus TCP or RTU | - | - | -
DG2-E-TOT | Generator controller DG2 | Energy total | Read | Counter | MWh | Modbus TCP or RTU | - | - | -
DG2-MODE | Generator controller DG2 | Controller mode | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG2-GCB | Generator controller DG2 | Breaker status | Read | Status | - | Modbus TCP or RTU | Status | - | -
DG2-WARN | Generator controller DG2 | Warning | Read | Status | - | Modbus TCP or RTU | 3 | On | -
DG2-SHUTDOWN | Generator controller DG2 | Shutdown alarm | Read | Status | - | Modbus TCP or RTU | 1 | On | -
DG2-START-CMD | Generator controller DG2 | Start | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG2-STOP-CMD | Generator controller DG2 | Stop | Write | Command | - | Modbus TCP or RTU | - | - | Operator | Only in manual mode
DG2-MODE-CMD | Generator controller DG2 | Mode auto / manual | Write | Command | - | Modbus TCP or RTU | - | - | Admin
AH1-I-L1 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-L2 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-L3 | 11 kV protection relay AH1 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-I-E | 11 kV protection relay AH1 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L1 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L2 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-U-L3 | 11 kV protection relay AH1 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH1-P | 11 kV protection relay AH1 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH1-Q | 11 kV protection relay AH1 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH1-PF | 11 kV protection relay AH1 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH1-F | 11 kV protection relay AH1 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH1-E-IMP | 11 kV protection relay AH1 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH1-E-EXP | 11 kV protection relay AH1 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH1-CB-POS | 11 kV protection relay AH1 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH1-TRIP-50 | 11 kV protection relay AH1 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-50N | 11 kV protection relay AH1 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-27-59 | 11 kV protection relay AH1 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-TRIP-81 | 11 kV protection relay AH1 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH1-RLY-HEALTHY | 11 kV protection relay AH1 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH1-DREC | 11 kV protection relay AH1 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH1-TCS-ALM | 11 kV protection relay AH1 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH1-TRIP-51G | 11 kV protection relay AH1 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH1-TRIP-32 | 11 kV protection relay AH1 | Reverse power trip (32), AH1 generator incomer | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Protects the generators against reverse power from PV and battery
AH2-I-L1 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-L2 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-L3 | 11 kV protection relay AH2 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-I-E | 11 kV protection relay AH2 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L1 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L2 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-U-L3 | 11 kV protection relay AH2 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH2-P | 11 kV protection relay AH2 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH2-Q | 11 kV protection relay AH2 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH2-PF | 11 kV protection relay AH2 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH2-F | 11 kV protection relay AH2 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH2-E-IMP | 11 kV protection relay AH2 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH2-E-EXP | 11 kV protection relay AH2 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH2-CB-POS | 11 kV protection relay AH2 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH2-TRIP-50 | 11 kV protection relay AH2 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-50N | 11 kV protection relay AH2 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-27-59 | 11 kV protection relay AH2 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-TRIP-81 | 11 kV protection relay AH2 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH2-RLY-HEALTHY | 11 kV protection relay AH2 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH2-DREC | 11 kV protection relay AH2 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH2-TCS-ALM | 11 kV protection relay AH2 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH2-TRIP-51G | 11 kV protection relay AH2 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH3-I-L1 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-L2 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-L3 | 11 kV protection relay AH3 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-I-E | 11 kV protection relay AH3 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L1 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L2 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-U-L3 | 11 kV protection relay AH3 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH3-P | 11 kV protection relay AH3 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH3-Q | 11 kV protection relay AH3 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH3-PF | 11 kV protection relay AH3 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH3-F | 11 kV protection relay AH3 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH3-E-IMP | 11 kV protection relay AH3 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH3-E-EXP | 11 kV protection relay AH3 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH3-CB-POS | 11 kV protection relay AH3 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH3-TRIP-50 | 11 kV protection relay AH3 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-50N | 11 kV protection relay AH3 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-27-59 | 11 kV protection relay AH3 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-TRIP-81 | 11 kV protection relay AH3 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH3-RLY-HEALTHY | 11 kV protection relay AH3 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH3-DREC | 11 kV protection relay AH3 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH3-TCS-ALM | 11 kV protection relay AH3 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH3-TRIP-51G | 11 kV protection relay AH3 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH4-I-L1 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-L2 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-L3 | 11 kV protection relay AH4 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-I-E | 11 kV protection relay AH4 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L1 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L2 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-U-L3 | 11 kV protection relay AH4 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH4-P | 11 kV protection relay AH4 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH4-Q | 11 kV protection relay AH4 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH4-PF | 11 kV protection relay AH4 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH4-F | 11 kV protection relay AH4 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH4-E-IMP | 11 kV protection relay AH4 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH4-E-EXP | 11 kV protection relay AH4 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH4-CB-POS | 11 kV protection relay AH4 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH4-TRIP-50 | 11 kV protection relay AH4 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-50N | 11 kV protection relay AH4 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-27-59 | 11 kV protection relay AH4 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-TRIP-81 | 11 kV protection relay AH4 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH4-RLY-HEALTHY | 11 kV protection relay AH4 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH4-DREC | 11 kV protection relay AH4 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH4-TCS-ALM | 11 kV protection relay AH4 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH4-TRIP-51G | 11 kV protection relay AH4 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH5-I-L1 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-L2 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-L3 | 11 kV protection relay AH5 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-I-E | 11 kV protection relay AH5 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L1 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L2 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-U-L3 | 11 kV protection relay AH5 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH5-P | 11 kV protection relay AH5 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH5-Q | 11 kV protection relay AH5 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH5-PF | 11 kV protection relay AH5 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH5-F | 11 kV protection relay AH5 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH5-E-IMP | 11 kV protection relay AH5 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH5-E-EXP | 11 kV protection relay AH5 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH5-CB-POS | 11 kV protection relay AH5 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH5-TRIP-50 | 11 kV protection relay AH5 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-50N | 11 kV protection relay AH5 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-27-59 | 11 kV protection relay AH5 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-TRIP-81 | 11 kV protection relay AH5 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH5-RLY-HEALTHY | 11 kV protection relay AH5 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH5-DREC | 11 kV protection relay AH5 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH5-TCS-ALM | 11 kV protection relay AH5 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH6-I-L1 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-L2 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-L3 | 11 kV protection relay AH6 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-I-E | 11 kV protection relay AH6 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L1 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L2 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-U-L3 | 11 kV protection relay AH6 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH6-P | 11 kV protection relay AH6 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH6-Q | 11 kV protection relay AH6 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH6-PF | 11 kV protection relay AH6 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH6-F | 11 kV protection relay AH6 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH6-E-IMP | 11 kV protection relay AH6 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH6-E-EXP | 11 kV protection relay AH6 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH6-CB-POS | 11 kV protection relay AH6 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH6-TRIP-50 | 11 kV protection relay AH6 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-50N | 11 kV protection relay AH6 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-27-59 | 11 kV protection relay AH6 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-TRIP-81 | 11 kV protection relay AH6 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH6-RLY-HEALTHY | 11 kV protection relay AH6 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH6-DREC | 11 kV protection relay AH6 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH6-TCS-ALM | 11 kV protection relay AH6 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH6-TRIP-51G | 11 kV protection relay AH6 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
AH7-I-L1 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-L2 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-L3 | 11 kV protection relay AH7 | Phase current L1, L2, L3 (3 points) | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-I-E | 11 kV protection relay AH7 | Earth current | Read | Measured | A | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L1 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L2 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-U-L3 | 11 kV protection relay AH7 | Voltage L1, L2, L3 (3 points) | Read | Measured | kV | IEC 61850 or Modbus TCP | - | - | -
AH7-P | 11 kV protection relay AH7 | Active power | Read | Measured | kW | IEC 61850 or Modbus TCP | - | - | -
AH7-Q | 11 kV protection relay AH7 | Reactive power | Read | Measured | kvar | IEC 61850 or Modbus TCP | - | - | -
AH7-PF | 11 kV protection relay AH7 | Power factor | Read | Measured | - | IEC 61850 or Modbus TCP | - | - | -
AH7-F | 11 kV protection relay AH7 | Frequency | Read | Measured | Hz | IEC 61850 or Modbus TCP | - | - | -
AH7-E-IMP | 11 kV protection relay AH7 | Energy import | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH7-E-EXP | 11 kV protection relay AH7 | Energy export | Read | Counter | MWh | IEC 61850 or Modbus TCP | - | - | -
AH7-CB-POS | 11 kV protection relay AH7 | Breaker position | Read | Double point | - | IEC 61850 or Modbus TCP | Status | - | -
AH7-TRIP-50 | 11 kV protection relay AH7 | Overcurrent trip (50/51) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-50N | 11 kV protection relay AH7 | Earth fault trip (50N/51N) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-27-59 | 11 kV protection relay AH7 | Under / overvoltage trip (27/59) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-TRIP-81 | 11 kV protection relay AH7 | Frequency trip (81) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | -
AH7-RLY-HEALTHY | 11 kV protection relay AH7 | Relay healthy | Read | Status | - | IEC 61850 or Modbus TCP | 2 | Off | -
AH7-DREC | 11 kV protection relay AH7 | Disturbance record available | Read | Status | - | IEC 61850 or Modbus TCP | 3 | On | -
AH7-TCS-ALM | 11 kV protection relay AH7 | Trip circuit supervision alarm | Read | Status | - | IEC 61850 or Modbus TCP | 2 | On | - | Added rev 1
AH7-TRIP-51G | 11 kV protection relay AH7 | Sensitive earth fault trip (51G) | Read | Event | - | IEC 61850 or Modbus TCP | 1 | On | - | Added rev 1. Panels with a zero-sequence CT (all except AH5)
PRS-RLY-I-L1 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PRS-RLY-I-L2 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PRS-RLY-I-L3 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PRS-RLY-I-E | RMU relay ST260E | Earth current | Read | Measured | A | Modbus RTU through MGate | - | - | -
PRS-RLY-CB-POS | RMU relay ST260E | Breaker position | Read | Double point | - | Modbus RTU through MGate | Status | - | -
PRS-RLY-TRIP-50 | RMU relay ST260E | Overcurrent trip | Read | Event | - | Modbus RTU through MGate | 1 | On | -
PRS-RLY-TRIP-50N | RMU relay ST260E | Earth fault trip | Read | Event | - | Modbus RTU through MGate | 1 | On | -
PRS-RLY-RLY-HEALTHY | RMU relay ST260E | Relay healthy | Read | Status | - | Modbus RTU through MGate | 2 | Off | -
PMS-RLY-I-L1 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PMS-RLY-I-L2 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PMS-RLY-I-L3 | RMU relay ST260E | Phase current L1, L2, L3 (3 points) | Read | Measured | A | Modbus RTU through MGate | - | - | -
PMS-RLY-I-E | RMU relay ST260E | Earth current | Read | Measured | A | Modbus RTU through MGate | - | - | -
PMS-RLY-CB-POS | RMU relay ST260E | Breaker position | Read | Double point | - | Modbus RTU through MGate | Status | - | -
PMS-RLY-TRIP-50 | RMU relay ST260E | Overcurrent trip | Read | Event | - | Modbus RTU through MGate | 1 | On | -
PMS-RLY-TRIP-50N | RMU relay ST260E | Earth fault trip | Read | Event | - | Modbus RTU through MGate | 1 | On | -
PMS-RLY-RLY-HEALTHY | RMU relay ST260E | Relay healthy | Read | Status | - | Modbus RTU through MGate | 2 | Off | -
PRS-LV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PRS-LV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PRS-LV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
PRS-LV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
PRS-LV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
PRS-LV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
PRS-LV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
PRS-LV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
PRS-LV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
PRS-LV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
PRS-LV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
PMS-LV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
PMS-LV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
PMS-LV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
PMS-LV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
PMS-LV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
PMS-LV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
PMS-LV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
PMS-LV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
PMS-LV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
PMS-LV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
PMS-LV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
AUXLV-U-L1N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-U-L2N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-U-L3N | Power meter PM5560 | Voltage L-N, 3 phases (3 points) | Read | Measured | V | Modbus TCP | - | - | -
AUXLV-I-L1 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-I-L2 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-I-L3 | Power meter PM5560 | Current, 3 phases (3 points) | Read | Measured | A | Modbus TCP | - | - | -
AUXLV-P | Power meter PM5560 | Active power | Read | Measured | kW | Modbus TCP | - | - | -
AUXLV-Q | Power meter PM5560 | Reactive power | Read | Measured | kvar | Modbus TCP | - | - | -
AUXLV-S | Power meter PM5560 | Apparent power | Read | Measured | kVA | Modbus TCP | - | - | -
AUXLV-PF | Power meter PM5560 | Power factor | Read | Measured | - | Modbus TCP | - | - | -
AUXLV-F | Power meter PM5560 | Frequency | Read | Measured | Hz | Modbus TCP | - | - | -
AUXLV-E-P | Power meter PM5560 | Active energy | Read | Counter | kWh | Modbus TCP | - | - | -
AUXLV-E-Q | Power meter PM5560 | Reactive energy | Read | Counter | kvarh | Modbus TCP | - | - | -
AUXLV-THD-U | Power meter PM5560 | Voltage THD | Read | Measured | % | Modbus TCP | - | - | -
AUXLV-THD-I | Power meter PM5560 | Current THD | Read | Measured | % | Modbus TCP | - | - | -
WS-IRR-POA | Weather logger blue'Log XM | Plane-of-array irradiance | Read | Measured | W/m2 | Modbus TCP | - | - | -
WS-WIND-SPD | Weather logger blue'Log XM | Wind speed | Read | Measured | m/s | Modbus TCP | - | - | -
WS-WIND-DIR | Weather logger blue'Log XM | Wind direction | Read | Measured | deg | Modbus TCP | - | - | -
WS-T-AMB | Weather logger blue'Log XM | Ambient temperature | Read | Measured | deg C | Modbus TCP | - | - | -
WS-T-MOD | Weather logger blue'Log XM | Module temperature | Read | Measured | deg C | Modbus TCP | - | - | -
WS-HEALTHY | Weather logger blue'Log XM | Logger healthy | Read | Status | - | Modbus TCP | 2 | Off | -
UPS-U-IN | UPS | Input voltage | Read | Measured | V | Modbus TCP or SNMP | - | - | -
UPS-LOAD | UPS | Output load | Read | Measured | % | Modbus TCP or SNMP | - | - | -
UPS-BATT-CHG | UPS | Battery charge | Read | Measured | % | Modbus TCP or SNMP | - | - | -
UPS-RUNTIME | UPS | Runtime remaining | Read | Measured | min | Modbus TCP or SNMP | - | - | -
UPS-ON-BATT-COM | UPS | On battery | Read | Status | - | Modbus TCP or SNMP | 2 | On | - | Communicated copy of hardwired signal UPS-ON-BATT
UPS-FLT-COM | UPS | Fault | Read | Status | - | Modbus TCP or SNMP | 2 | On | - | Communicated copy of hardwired signal UPS-FLT
SW-CORE-A-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-A-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-B-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-CORE-B-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-MV-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-MV-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-BESS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-BESS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-GEN-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-GEN-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PRS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PRS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PMS-HEALTHY | Network switches (core and field) | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
SW-PMS-RING-OK | Network switches (core and field) | Ring status | Read | Status | - | SNMP v3 | 2 | Off | -
FW-HEALTHY | Firewall and GPS time server | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
FW-VPN-ACTIVE | Firewall and GPS time server | Time synchronised / VPN session active | Read | Status | - | SNMP v3 | 3 | On | -
GPS-HEALTHY | Firewall and GPS time server | Device healthy | Read | Status | - | SNMP v3 | 2 | Off | -
GPS-TIME-SYNC | Firewall and GPS time server | Time synchronised / VPN session active | Read | Status | - | SNMP v3 | 3 | Off | -
PLCBOX-NB01-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB02-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB03-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
PLCBOX-NB04-COMM | PLC box | Communication healthy per inverter (4 points) | Read | Status | - | Modbus TCP | Status | - | -
CP-HEALTHY | SICAM CP-8050 internal | Controller healthy | Read | Status | - | Internal | 2 | Off | -
CP-PS1-OK | SICAM CP-8050 internal | Power supply 1 healthy | Read | Status | - | Internal | 2 | Off | -
CP-PS2-OK | SICAM CP-8050 internal | Power supply 2 healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW1-OK | SICAM CP-8050 internal | I/O row 1 healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW2-OK | SICAM CP-8050 internal | I/O row 2 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW3-OK | SICAM CP-8050 internal | I/O row 3 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW4-OK | SICAM CP-8050 internal | I/O row 4 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW5-OK | SICAM CP-8050 internal | I/O row 5 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-ROW6-OK | SICAM CP-8050 internal | I/O row 6 link healthy | Read | Status | - | Internal | 2 | Off | -
CP-LINK1-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK2-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK3-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK4-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK5-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK6-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK7-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -
CP-LINK8-OK | SICAM CP-8050 internal | Link to each communication device healthy (8 links) | Read | Status | - | Internal | 2 | Off | -

## Datasheets
No. | Group | Item | Manufacturer | Model | Order no. to search | Documents to collect | Where to download | Collected
1 | Controller | Processor module | Siemens | SICAM A8000 CP-8050 | 6MF2805-0AA00 | Datasheet; CP-8050 system manual; security manual | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
2 | Controller | Power supply | Siemens | SICAM A8000 PS-8642 | 6MF2864-2AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
3 | Controller | Ethernet interface | Siemens | SICAM A8000 CI-8520 | 6MF2852-0AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
4 | Controller | Flash card | Siemens | SICAM flash card 2 GB | 6MF1213-1GA05-0AA0 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
5 | I/O | Digital input module | Siemens | SICAM A8000 DI-8112 | 6MF2811-2AA00 | Datasheet (confirm input voltage) | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
6 | I/O | Secured command output | Siemens | SICAM A8000 DO-8221 | Ask Siemens | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
7 | I/O | Relay output module | Siemens | SICAM A8000 DO-8212 | 6MF2821-2AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
8 | I/O | Analogue input module | Siemens | SICAM A8000 AI-8320 | 6MF2832-0AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
9 | I/O | Remote interface, electrical | Siemens | SICAM A8000 CI-8532 | 6MF2853-2AA00 | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
10 | I/O | Remote interface, optical | Siemens | SICAM A8000 CI-8533 | Ask Siemens | Datasheet, incl. fibre type and maximum length | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
11 | I/O | SICAM A8000 series | Siemens | SICAM A8000 catalogue | - | Catalogue / module overview | Siemens SICAM A8000 product page (siemens.com, search 'SICAM A8000')
12 | SCADA | SCADA servers | Siemens | SIMATIC IPC647E | Configured order no. | Datasheet | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
13 | SCADA | Operator workstation | Dell | OptiPlex 7000 series | Configured | Specification sheet | dell.com, product page 'OptiPlex 7000', Specifications
14 | SCADA | Engineering laptop | Dell | Latitude 5430 Rugged | Configured | Specification sheet | dell.com, product page 'Latitude 5430 Rugged', Specifications
15 | Network | Core switches | Siemens or Moxa | SCALANCE XC216-4C (or Moxa EDS-G512E) | Per final choice | Datasheet; substation rating if any | SIOS for SCALANCE; moxa.com product page for Moxa
16 | Network | Field and station switches | Siemens or Moxa | SCALANCE XC208 / XC206-2SFP EEC (or Moxa EDS-510E) | Per final choice | Datasheet | SIOS for SCALANCE; moxa.com product page for Moxa
17 | Network | Fibre transceivers | Siemens or Moxa | SCALANCE SFP992-1LD (or Moxa SFP-1GLXLC) | Per final choice | Datasheet | SIOS for SCALANCE; moxa.com product page for Moxa
18 | Network | Serial gateway for RMU relays | Moxa (or Siemens RUGGEDCOM) | MGate MB3170 (or RUGGEDCOM RS416 / RMC30) | Per final choice | Datasheet | moxa.com product page; or siemens.com RUGGEDCOM pages
19 | Network | Firewall and VPN | Siemens or Fortinet | SCALANCE SC646-2C (or FortiGate Rugged 60F) | Per final choice | Datasheet | SIOS for SCALANCE; fortinet.com data sheets library for FortiGate Rugged
20 | Network | GPS time server | Meinberg | LANTIME M300/GPS | M300/GPS | Datasheet | meinbergglobal.com, product page LANTIME M300
21 | Power | Power meters | Schneider Electric | PowerLogic PM5560 | METSEPM5560 | Datasheet; Modbus register list | se.com, search 'METSEPM5560', Documents
22 | Power | 24 V DC power supplies | Siemens | SITOP PSU8200 24 V/20 A | 6EP1336-3BA10 | Datasheet; SITOP PSU8200 1-phase manual | Siemens Industry Online Support (support.industry.siemens.com): search the order number, tab 'Product information' or 'Manuals'
23 | Power | UPS | APC (Schneider Electric) | Smart-UPS SRT 3000 VA | SRT3000RMXLI | Datasheet | apc.com or se.com, search 'SRT3000RMXLI'
24 | Enclosure | SCADA cabinet | Rittal | VX25 800 x 2000 x 800 | 8808.000 | Datasheet | rittal.com, search '8808.000'
25 | Enclosure | Outdoor I/O panels | Rittal | AX, size to suit | Per size | Datasheet | rittal.com, AX compact enclosures
26 | Enclosure | Alarm sounder and beacon | Pfannenberg | PATROL series | Per model | Datasheet | pfannenberg.com, PATROL series
27 | Software | Substation SCADA | Siemens | SICAM SCC | Per licence quote | Product description; system requirements; licensing | Siemens SICAM SCC product page; documents via SIOS
28 | Software | Controller engineering tool | Siemens | SICAM Device Manager | Per licence quote | Product information; system requirements | Siemens SICAM A8000 / Device Manager pages; SIOS
29 | Software | Network management | Siemens or Moxa | SINEC NMS (or Moxa MXview One) | Per licence quote | Product information | SIOS for SINEC NMS; moxa.com for MXview One
30 | Software | Remote access management | Siemens or Fortinet | SINEMA Remote Connect (or FortiClient) | Per licence quote | Product information | SIOS for SINEMA RC; fortinet.com for FortiClient
31 | Software | Operating systems | Microsoft | Windows Server, Windows 11 Pro | - | Not usually requested; licence certificates at delivery | -
32 | Field device | PV inverters | Sungrow | SG350HX | - | Datasheet; communication protocol | sungrowpower.com product page; or PV designer
33 | Field device | Power line communication box | Sungrow | TBC | - | Datasheet; Modbus point table | PV designer
34 | Field device | Battery system | Sungrow | ST3340UX | - | Datasheet; communication protocol | Battery supplier
35 | Field device | Embedded EMS | TBC | TBC | - | Datasheet; Modbus point table | PV designer
36 | Field device | Generator controllers | TBC | TBC | - | Datasheet; Modbus point table | Generator supplier
37 | Field device | 11 kV protection relays | TBC | TBC | - | Datasheet; IEC 61850 or Modbus documentation | Switchgear supplier
38 | Field device | RMU relays | Per RMU supplier | ST260E | - | Datasheet; Modbus map | RMU supplier
39 | Field device | Fire detection and suppression panel | TBC | TBC | - | Datasheet; contact schedule | Fire system supplier
40 | Field device | Weather logger | Meteocontrol | blue'Log XM | - | Datasheet; Modbus documentation | meteocontrol.com product page
41 | Field device | Pyranometer | Kipp & Zonen | SMP12-A | - | Datasheet | kippzonen.com / otthydromet.com product page
42 | Field device | Wind sensor | Gill Instruments | WindSonic RS485 | - | Datasheet | gillinstruments.com product page
Fill the Collected column as each file is saved. Name files '<No.>_<Model>.pdf' so they sort in this order inside the zip.
Network items list both Siemens SCALANCE and Moxa/Fortinet; collect only the final choice.